## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
A | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
A.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangement with ceiling / wall etc. (Make: Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent with airport approval)
A.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 4
A.1.2 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 1
A.1.3 | Upright Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 4
FIRE SPRINKLER PIPE VALVES & ACCESSORIES
A.3 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.)
A.3.1 | 50 mm Dia | Nos | 1
A.4 | Supply, Installation, Testing & Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem & lever, with necessary weldable fittings in position as per drawings / site conditions. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.)
A.4.1 | 25 mm Dia | Nos | 1
A.5 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. (Make: Potter/ System Sensor or equivalent with airport approval)
A.5.1 | 50 mm Dia | Nos | 1
FIRE SPRINKLER PIPING
A.6 | Supply, Installation, Testing & Commissioning of MS "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) (Make: HSL, Mukut, Lalit steel or equivalent)
A.6.1 | 25 mm Dia | Mtr | 12
A.6.2 | 40 mm Dia | Mtr | 4
A.6.3 | 50 mm Dia | Mtr | 7