## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
| - | - | -
| SPLIT UNITS - DUCTABLE UNITS & HIWALL UNITS | - | -
| Removal of existing 8.5TR Ductable Indoor Units & storing them in a good condition | - | -
| 8.5TR Ductable Unit | Nos | 8
| - | - | -
| Re-Installation of existing 8.5TR Ductable Units. Vaccumizing, pressure testing, gas charging & commissioning of the same | - | -
| 8.5TR Ductable Unit | Nos | 8
| - | - | -
| Gas Required for commissioning | Kgs | 50
| - | - | -
| Indoor Stands for 8.5TR Ductable Unit | Nos | 8
| - | - | -
| Epoxy paint, Enamel paint & modification if required for existing outdoor unit stand | Nos | 8
| - | - | -
| 1.5TR Hiwall Split Unit ( 3 Star ) | Nos | 0
| - | - | -
| REFRIGERANT COPPER PIPING FOR DUCTABLE UNITS | - | -
| Supply, installation, testing & commissioning of refrigerant copper piping connected between odu unit & IDU units covered with19 mm thick XLPE insulation. | - | -
| Liquid& Gas Cu Piping with 19mm Al Faced XLPE insulation for Ductable Unit | Rmt | 10
| Liquid& Gas Cu Piping with 19mm Al Faced XLPE insulation for Hiwall Unit | Rmt | 2
| - | - | -
| Communication Cable if required. Existing cable will be used. 3 Core x 2.5 Sqm Shielded Copper Cable in PVC Conduits(ODU TO IDU) | Rmt | 0
| - | - | -
| - | - | -
| FAN | - | -
| Supply, installation, commissioning & testing of Inline fans (Exhaust & Fresh Air Fan) | - | -
| Capacity: 400 cfm @ 15 mm WC static pressure- Fresh Air Fan | Nos | RO
| Capacity: 500 cfm @ 15 mm WC static pressure - Fresh Air Fan | Nos | RO
| Capacity: 500 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | RO
| Capacity: 700 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | RO
| - | - | -
| CONDENSATE DRAIN PIPING | - | -
| Supply, installation, testing & Commissioning of PVC drain pipe of following sizes with 9mm thick XLPE insulation. | - | -
| 50mm dia With 9mm XLP insulation | Rmt | 35
| 40mm dia With 9mm XLP insulation | Rmt | 12
| 32mm dia With 9mm XLP insulation | Rmt | 15
| 25mm dia With 9mm XLP insulation | Rmt | RO
| - | - | -
| DUCTWORK & ACCESSORIES | - | -
| Rectangular Ducting | - | -
| 24G -Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle / rod / wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible connections, etc.) | Sq.m | 265
| 22G - Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle / rod / wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible connections, etc.) | Sq.m | 125
| - | - | -
| Supply, Installation, testing & commissioning of factory built Manual Volume Control Dampers | Sq.m | 2
| - | - | -
| Supply, Installation, testing & commissioning of factory built Collar Volume Control Dampers | Sq.m | 11
| - | - | -
| Supply, Installation, testing & commissioning of factory built Fire Control Dampers | Sq.m | RO
| - | - | -
| Fusible Link for Fire Control Dampers | Nos | RO
| - | - | -
| Supply, Installation, testing & commissioning of factory built AL Birdscreen with louvers | Sq.m | 1
| - | - | -
| Insulated Plenum boxes 200 x 300 x 650 | Nos | 80
| - | - | -
| SITC and balancing of grills and deffusers | - | -
| 3 slot grills for supply air with hit and miss dampers complete with air patern controller. | RM | 70
| 3 slot grills for return air without dampers complete with air patern controller. | RM | RO
| Linear Air Grilles with Al. VCD - Linear Fixed Bar Grilles, Horizontal Fixed with removable cores, core styles 1/2/3 way with opposed Blade aluminium Bars, Normal Blade (5 mm nominal thickness) Grille height 16 mm, blade pitch 12.5 mm. 150mm wide linear grilles without dampers | Sq.m | 0
| Linear Air Grilles without VCD - Linear Fixed Bar Grilles for Return Air 150mm wide linear grilles without dampers | Sq.m | 12
| - | - | -
| DIFFUSER | - | -
| Supply Air Diffusers with Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1/2/3 way with opposed Blade aluminium extruded construction VCD Black Anodized | Nos | RO
| Return Air Diffusers without Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1/2/3 way with opposed Blade aluminium extruded construction. | Nos | RO
| - | - | -
| Supply and installation of return air Disc valve (TOILET EXHAUST & FRESH AIR) | - | -
| 150dia | Nos | RO
| - | - | -
| Supply Installation testing and comissioning of insulated flexible duct of given sizes. Make Twiga or equal | - | -
| - | - | -
| Dia 200 | Rmt | 60
| - | - | -
| GI Rings for Flexible Connections | - | -
| 200 Dia | Nos | 160
| 300 Dia | Nos | RO
| - | - | -
| Return air Z Piece ( 300 x 300 x 900 ) with Insulation | Nos | RO
| - | - | -
| INSULATIONS-HVAC | - | -
| Thermal duct insulation : | - | -
| 13mm thick Al.Faced XLPE insulation ('Aerofoam' or approved equivalent) | Sq.m | 350
| - | - | -
| Duct Accoustic Insulation | - | -
| Acoustic insulation of Ducts - Physically crosslinked Open cell polyolefin foam with factory applied reinforced aluminium foil having density of 25kg/m3 and meeting the Class 0 requirements of Fire safety as per BS 476 Part 6 & 7.The material shall be antifungal in nature and tested to ASTM G21 standard The NRC of 15mm thick material would be 0.4 when tested as per ISO 354 standard. 25mm ( Self Adhesive Only ) Approved Makes - Aerofoam / Thermobreak or equal | Sq.m | 125
| - | - | -
| Under deck Insulastion | - | -
| Insulation material shall be Closed Cell Elastomeric Armaflex Nitrile Rubber, Density of Material shall be between 45 + 5 kg/m3, Thermal conductivity of elastomeric nitrile rubber shall not exceed 0.035 W/mK at mean temperature of 0C,• The insulation shall have fire performance such that it passes Class 1 as per BS476 Part 7 for surface spread of flame and also pass Fire Propagation requirement as per BS476 Part 6 to meet the Class ‘O’ Fire category, Material should be FM (Factory Mutual), USA approved, Moisture Diffusion Resistance Factor ‘µ’ value should be minimum 7000For Concrete Slab: 25 mm thick sheet is used & For Corrugated or metal ceiling: 32 mm thick sheet | Sq.m. | 330
| - | - | -
| Scaffolding for Ducting work at Double height area. | Lot | 1
| - | - | -
| - | - | -
| - | - | -
| - | - | -
| - | - | -
| Taxes Extra as applicable | - | -