## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
1 | Air Handling Unit
Supply, Installation, Testing and Commissioning of Horizontal draw, Double Skin sheet metal sectionalised construction Air Handling units with injected PUF in between. Complete with pre-filter section, fan section complete with floor standing forward curved DIDW centrifugal fan, belt drive package, base frame, squirrel cage TEFC induction motor & vibration isolation pads, wet section with S.S Tray, drain Point. AHU shall be designed as per specifications. Including flexible canvas connections made of fire resistance flexible double canvas sleeve for duct connection. Air Handling Unit shall be selected for a maximum face velocity of 500 FPM at filter section and 500 FPM at cooling Coil. Blower Make : - Humidin / Fanair/ Blowtech/Equivalant
Air Handling Unit
Outer skin = 0.6 mm pre-coated GSS
Inner skin = 0.6 mm plain GSS
Panel = 23 ± 2 mm thick PU Foam density 40 kg/m3
Frame Work = Extruded Aluminium
Tank = 18G SS-304
Hinges and Locks = Aluminium Die cast
Cooling Coil = 4RD Chilled Water Cooling coil
Fan Section
Outer skin = 0.6 mm pre-coated GSS
Inner skin = 0.6 mm plain GSS
Panel = 25 mm thick PU Foam density 40 kg/m3
Frame Work = Extruded Aluminium
Fan & Motor detail
Fan Size = 315 Dia(Forward Curved)
Motor = 2.2 KW
| Air Handling Unit - 3000 CFM @50 mmwg | Nos. | 1
2 | Dry Scrubber Units With Differential pressure sensor for giving signal at panel
Installation, testing and Commissioning of Double skin dry type scrubber section with required accessories for Exhaust Purpose.The unit shall include the differential pressure sensor for giving signal at panel Fan Make: Kruger/Nicotra/Blowtech. Motor : Crompton/Havells/BB/Siemens/Hindustan Motors.
2.1 | 4000 CFM (with Backward Type DIDW Blowers) 3.75 KW Motor ; SP 60 mm of wg;for Kitchen Exhaust | Nos. | 1
3 | Package Type Air Washers-Double Skin Construction
Installation, testing and Commissioning of Double Skin Packaged Type Air Washer with extruded aluminium section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, 25 mm thick PUF insulation of 42KG/m3 , G.I. blower section, DIDW Blower (Backward Curved) / Plug Fans with motors , base , drive arrangement ,Filter, cooling pad section, stainless steel sump tank and housing, motor drive, water circulation pump, piping, valves & fittings etc. suitable for Outdoor Application as per specifications and drawings .The cost shall include the Differential Pressure Sensor (Digital Type) across the filter .
3.1 | 3500 CFM (with Backward Type DIDW Blowers) 2.2 KW Motor ; SP 50 mm of wg;for Kitchen Fresh Air Supply | Nos. | 1
Note:-
1. GST shall be charged extra as applicable.
2. All electrical work upto Air Handling Unit shall be in client scope.
3. Final billing will be done on actual measurement basis.
4. Any extra item apart from BOQ will be chargable basis.
5. All Machine Plateform shall be in Client Scope.