## Summary
AJ KITCHEN - Bill Summary
S.N | Item | PO Value | RA-01 Value | PO No.
1 | Civil | 1085000 | 511522.645 | Semolina/PO/23-24/000456
2 | Electrical | 702600 | 169825 | Semolina/PO/23-24/000456
3 | Plumbing | 194260 | 132710 | Semolina/PO/23-24/000456
4 | HVAC | 805029 | 165589.911 | Semolina/PO/23-24/000470
5 | Gas | 127145.8 | 34217.56 | Semolina/PO/23-24/000598
6 | SUB TOTAL |  | 1013865.116
7 | GST -18% |  | 182495.7209
8 | TOTAL |  | 1196360.8369

## Civil & Interior
BOQ - Civil & Interior Work |  | PO |  |  |  | RA-01
S.N | ItemName | UOM | Quantity | Rate | Amount | Qty | Amount
[5 empty] | 1085000 |  | 511522.645
1 | Supply and installation of fire rated calcium silicate board Partition Wall with the necessory supports, fittings and fixtures (excluding final finishes). Purposed height of kitchen partition wall is 4925mm and pot wash room is 3000mm, it may be change as per site conditions. Note Framing and double side board to be installed. Final Finishies price to be quoted in wall finishes section. | SQM | 41 | 3650 | 149650 | 40.7708 | 148813.42
2 | Supply and installation of fire rated calcium silicate board cladding on the existing walls in the Kitchen pot wash area to pass the MEP services to receive the final finishes with the necessory supports, fittings and fixtures (excluding final finishes). Purposed height is 3000mm, it may be change as per site conditions. Note Framing and single side board to be installed on existing wall. Final Finishies price to be quoted in wall finishes section. | SQM | 25 | 3000 | 75000 | 25 | 75000
3 | Supply and installation of fire rated Gypsum board cladding on the existing walls to pass the MEP services to receive the final finishes with the necessory supports, fittings and fixtures in the FOH dining area walls. (excluding final finishes). Purposed height is 3150mm, it may be change as per site conditions. Note Framing and single side board to be installed on existing wall. Final Finishies price to be quoted in wall finishes section. | SQM | 66 | 2400 | 158400 | 55.1145 | 132274.8
4 | 160mm thick concrete floor screeding to raise the floor to accomodate the drainage pipes and floor gratings to receive floor finish in the Kitchen FOH counter areas; all in accordance with drawings site conditions. Note Total height of floor to be raised including floor finishes is 200mm in the kitchen FOH counter area only | SQM | 28 | 700 | 19600 | 28 | 19600
5 | Wet Areas 2 Layers of 4mm thick SBS Bituminous membrane with 24-hour water ponding test including the sealing of Cores in the slab walls (inspected and approved from airports team). | SQM | 34 | 1150 | 39100 | 4.0755 | 4686.825
6 | Supply and installation of self levelling with all necessary items; all in accordance with drawings. | SQM | 62 | 475 | 29450 | 0 | 0
7 | Supply and installation of anti-skid 600 x 600 mm white floor tile in the kitchen Pot wash area as per the drawings and renders. Note Material to be approved by Clients team. | SQM | 12 | 1700 | 20400 | 11.408 | 19393.6
8 | Supply and installation of Stone Plastic Composite (SPC) flooring in the FOH dining area area; colour design as per drawings render. Note material to be approved by Clients Team | SQM | 25 | 2000 | 50000
9 | Supply and installation of anti skid 300 x 300 mm designer floor tile in the FOH area; colour design as per drawings render. Note material to be approved by Clients Team | SQM | 26 | 1750 | 45500
10 | supply installation of 100mm wooden skirting matching wall color as per the renders drawings. Note material to be approved by Clients Team | RM | 28 | 300 | 8400
11 | Supply installation of 300x300 mm White wall tile in the kitchen Pot wash area as per drawings and renders. Note material to be approved by Clients Team. Considered Ceiling height in kitchen is 2800mm | SQM | 52 | 1600 | 83200 | 52 | 83200
12 | Allow sum for the supply and Installation of SS corner beeding on the corners of kitchen wall tiles. | LS | 1 | 5000 | 5000
13 | Supply Painiting of matt finish paint of approved color on the walls of dining FOH area as per the drawings renders Note Material to be approved by clients Team | SQM | 86 | 500 | 43000
14 | Supply installation of WOODEN MOULDING STRIP finished with paint of approved colour on the walls of Dining FOH area as per drawings and renders. Note Material to be approved by clients Team | RM | 187 | 200 | 37400 | 142.77 | 28554
15 | Supply installation of Wooden moulding strip finished with approved colour on the front elevation as per drawings and renders. Note Material to be approved by clients Team | RM | 4 | 350 | 1400
16 | Hood - Hot Cooking line 2400 L x 1000 W x 400 H mm | LS | 1 | 35700 | 35700
17 | Supply Installation of 600x600 mm metal tile ceiling in the Kitchen Pot wash area with necessary support, fixtures accessories as per drawings renders Note Material to be approved by Clients Team. | SQM | 12 | 3200 | 38400
18 | Supply and Installation of Metal 3x3cm mesh ceiling with fire rated hanging flowers in the FOH Dining areas including the final finishes with necessary support, fixtures accessories as per drawings renders. Note Material to be approved by Clients Team. This ceiling will be Mesh type so that flower can be hanged. | SQM | 23 | 1400 | 32200
19 | Supply and Installation of fire rated Gypsum false ceiling with cove (for cove lights provision) in the the FOH dining area with paint in White color finishes with necessary support, fixtures accessories as per drawings renders, refer to RCP layout. Including access panel door as per the MEP services and Cutting finishing for the AC grill diffuser and lights. Note Material to be approved by Clients Team. Running meter of cove has included in total quantity (32.45m) | SQM | 53 | 2900 | 153700
20 | Supply and painting with matt finish paint on the slab walls of void ceiling area of FOH dinning, including paints on all MEP services metal ceiling parts. Note color to be selected approved by Clients Team. | LS | 1 | 26000 | 26000
21 | Supply and installation of heavy duty single leaf both side swing fire rated wooden door (KITCHEN DOOR FLUSHED TO WALL INVISIBLE TYPE FINISHED WITH SAME WALL COLOUR) with the door frame for kitchen, including all the fittings accessories as per the drawings and renders. Groove to be provided as per drawing and render. Dim 2200H x 900W mm Note Door frame should not be visible from Customer dining area. | Nos | 1 | 18000 | 18000
22 | Allow sum for the closing of wall opening using foams. | LS | 1 | 5500 | 5500
23 | Allow sum for the Kitchen equipment equipment unloading and shifting till outlet | LS | 1 | 10000 | 10000

## Electrical Work
BOQ - Electrical Work |  | PO |  |  |  | RA-01
S.N | ItemName | UOM | Quantity | Rate | Amount | Qty | Amount
I | PANEL SWITCHGEAR |  |  |  | 702600 |  | 169825
1 | Supply, installation, testing commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process and duly powder coated using Siemens Grey Shade No. RAL 7032. The frame structure, doors and gland plates shall have 2.0 mm thick sheets and partitions shall be with 1.6 mm thick CRCA sheet. Base channel size 75 x 40 x 6 mm of ISMC shall be provided. The panel shall be dust and vermin proof with neoprene gasket. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus bar shall be of tinned Copper with epoxy supports and shall be insulated with colour coded heat shrink sleeves. The control wiring min. 2,5 Sq.mm shall be ZHLS type. The Panel shall be provided with CTs, phase indication lamps, meters, relays and all switchgear, etc. as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant. All componants for Switchgears shall be L T Legrand
a | Providing installing MAIN LT PANEL as per SLD Spec. | Set | 1 | 22820 | 22820
125 Amps 4 pole, 25kA MCCB as a Incomer with overload, short circuit Earth Fault protection, Energy manager with RS485 port for BMS connectivity 4A with SP MCB with 100 5A-3 Nos., 15VA, CL-1 CT s for metering of AE make and phase indicating lamps Vaishno make with SPMCB
Busbar chamber - 1 set, 4 pole 125A Tinned AL. Busbar with necessary
OUTGOINGS
i. | 32A 4P MCB – 1 Nos.
ii. | 40A 4P MCB – 2 Nos.
iii. | 63A 4P MCB – 3 Nos.
iv. | 80A 4P MCCB 16kA TM Based O C, S C release.
2 | Supply, installation, testing commissioning of Switchgears.(Standard Product)
b | Supply,Installation,Testing and Commissioning of 32 Amps,4Pole MCB for HVAC Outdoor Isolation all complete with mounting accessories. | Nos. | 1 | 1000 | 1000
c | Supply,Installation,Testing and Commissioning of 40 Amps, DP, MCB for UPS INVERTER Isolation all complete with mounting accessories for UPS. | Nos. | 2 | 1100 | 2200
p | 20A Rey roll socket complete with 32 amps DPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | Nos. | 9 | 800 | 7200
q | 5 15A Rey roll socket complete with 15 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | Nos. | 5 | 700 | 3500
II | INVERTER UPS
1 | Supply, Installation, testing and commissioning of 6 KVA UPS System Single Phase I C Single Phase O G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings the specifications. | Nos | 1 | 70000 | 70000
III | DISTRIBUTION BOARDS
Supply, installation, testing commissioning of Distribution Boards surface flush mounted with Double door containing MCB ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs RCCB should be of 30mA 100 mA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be D type and other MCBs shall be C category for lighting and raw power DB LEGRAND L T
1 | Lighting Distribution Board - LPDB | Nos. | 1 | 5000 | 5000 | 1 | 5000
8 WAY TPN DB
I C- 1 # 32A FP MCB , 10KA
SUB I C - 3 # 25A DP RCCB 30mA per phase
O G - 18 # 10A SP MCB
3 | Kitchen Power DB - (KPDB-1) | Nos. | 1 | 4200 | 4200 | 1 | 4200
12 WAY TPN DB
I C- 1 #80 A FP MCB
SUB I C- 3#63 DP ELCB 100mA per ph
O G - 30 # 16 20A SP MCB
4 | EMERGENCY LIGHTING DB (ELDB) | Nos. | 1 | 5200 | 5200 | 1 | 5200
12 way SPN DB
Incomer 40A DP RCBO 30mA
Outgoings 10 16 SP MCB, D Type – 8 Nos
TOTAL FOR DISTRIBUTION BOARDS
IV | CABLES ACCESSORIES
Supply installation of following LT XLPE FRLS cables (FINOLEX RR KABLE POLYCAB) rated for 600 1100 volts AC as per IS standard 1554 Part 1 with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20 mtrs and ten finally with metal identification tags showing the size and the location from to the specific Panel DB at both ends.
9 | 3.5C x 35 Sq. mm A2XFY | Mtr. | 100 | 400 | 40000
10 | 4C x 16 Sq. mm A2XFY | Mtr. | 20 | 400 | 8000
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 15 | 330 | 4950
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 15 | 400 | 6000
17 | 3C x 6sq. mm YWY cable ( Cu ) | Mtr. | 15 | 320 | 4800
18 | 3C x 4sq. mm YWY cable ( Cu ) | Mtr. | 40 | 270 | 10800
9 | 3.5C x 35 Sq. mm A2XFY | Nos. | 2 | 500 | 1000
10 | 4C x 16 Sq. mm A2XFY | Nos. | 4 | 450 | 1800
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | Nos. | 4 | 450 | 1800
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) | Nos. | 4 | 380 | 1520
17 | 3C x 6sq. mm YWY cable ( Cu ) | Nos. | 12 | 380 | 4560
V | WIRING ACCESSORIES
Notes
1) Rates for point wiring shall include supply installation of Wires wiring acccessories such as angle holders ceiling roses as required. conduits, conduit accessories such as junction boxes, Ts, elbows etc,Switches, sockets fixtures shall not be included in the point wiring rates. These will be counted paid separately.
1 | Supply, installation, testing commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included.
Averagepoint length of primary secondaryto be derived by Contractor, fromthe drawing provided AND+ -1MtrMeasured Radially
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | Nos. | 8 | 2250 | 18000 | 8 | 18000
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | Nos. | 25 | 1350 | 33750 | 25 | 33750
2 | Supply, installation, testing commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Switch Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same switch board where primary points are controlling. The Power points shall be measured in Nos. Cost of FRLS PVC conduits, 6A switch switch board and accessories shall be included.
a) | Primary Light points controlled by Switch (3R x 2.5 sqmm wire) | Nos. | 2 | 1675 | 3350 | 2 | 3350
c) | DB to SB SB to SB circuit wiring For Switch Operated Primary point @ SB to SB loop point. Wiring for switch board controlled by MCB already installed in DB by using 3 X 2.5 sq. mm flexible LSZH copper wires in 25mm GI conduits as per IS 9537 part-3 or surface mounted. | Mtrs | 10 | 2250 | 22500
3 | Supply, installation, testing commissioning of point wiring for Emargency light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of FRLS PVC conduits and accessories shall be included.
Averagepoint length of primary secondaryto be derived by Contractor, fromthe drawing provided AND+ -1MtrMeasured Radially
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | Nos. | 1 | 2500 | 2500 | 1 | 2500
5 | Providing point wiring for Raw Power points 1no. 6 16A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 4.0 sq. mm copper conductor wires and minimum 4.0 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect Consultant. (Cost of FRLS PVC Conduit Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be LSZH type ) Note Average primary secondary point length to be derived by Contractor, from the drawing site provided AND + - 1 Mtr Measured Radially.
a) | Primary Point | Nos. | 2 | 1650 | 3300 | 2 | 3300
b) | Secondary points | Nos. | 2 | 1500 | 3000 | 2 | 3000
6 | Providing point wiring for Raw Power points 1no. 6A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 2.5 sq. mm copper conductor wires and minimum 2.5 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect Consultant. (Cost of Conduit Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be FRLS type ) Note Average primary secondary point length to be derived by Contractor, from the drawing site provided AND + - 1 Mtr Measured Radially.
a) | Primary Point | Nos. | 4 | 1200 | 4800 | 4 | 4800
b) | Secondary points | Nos. | 6 | 1100 | 6600 | 6 | 6600
8 | Supply and laying of following PVC insulated copper conductor 1100 volt grade stranded flexible LSZH wire in already laid GI conduit concealed or surface mounted making connections where ever required to complete the installation.(For Kitchen and Bar Power Points) Conduit rate shall be paid separately.
a) | 2R x 2.5Sqmm + 1R x 2.5Sqmm Cu. Wires | Mtr. | 120 | 200 | 24000 | 105 | 21000
b) | 3R x 4Sqmm Cu. Wires | Mtr. | 228 | 300 | 68400 | 150 | 45000
9 | Supply installation of 25 mm dia. GI conduit with pull box junction box all accessories for Kitchen Bar Power wiring as per the requirement
a | - do - but conduit pipe shall be Rigid type. | Mtr. | 225 | 55 | 12375 | 225 | 12375
b | - do - but flexible conduit pipe | Mtr. | 25 | 70 | 1750 | 25 | 1750
11 | Supply and installation of Perforated Cable Tray (ASIAN)out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant Architect
c | 150 x 50 x 2mm | Mtr. | 25 | 850 | 21250
12 | Supply and installation of GI trunking (SV POWER ASIAN) with 2 mm thickness properties clamps for suspension at appropriate intervals as per the route approved by Architect Consultant. (For DATA CONTROL WIRING LIGHTING POWER CIRCUITS KITCHEN)
e | 50 x 50 x 2mm | Mtr. | 20 | 650 | 13000
14 | Supply installation of GI junction boxes with 2 mm thickness, 2mm thick SS cover with 2” extra on all sides SS cover on top and having screw fixed plates on all four sides with knock out holes for conduits. The plates shall be retained on the sidezs having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be prepared as per the final approval of Architect Consultant. The junction boxes shall be protected from the entry of unwanted material till the completion of the project the SS plates shall be installed after the final polishing of flooring.
d | suitable for 150 x 150 x 50 mm | Nos. | 2 | 500 | 1000
15 | Supply, installation, testing commissioning of flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect Consultant
a | 6A one way plate type switch | Nos. | 4 | 80 | 320
c | 6A 5pin switch socket outlet for CCTV Charging point | Nos. | 12 | 90 | 1080
h | 1 nos. 6 16A socket controlled by1nos 6 16A switch | Nos. | 30 | 350 | 10500
l | I phase, 2 Nos x 5 15 amp, bakelite socket switch, housed in Fabricated SS Panel suitable for hanging arrangement for Kitchen equipments. (having Two outlet 6 modular plate) | Nos. | 1 | 4000 | 4000
17 | Supply, installation of temporary lighting power arrangement for construction purpose of with industrial type switch sockets MCB s ELCB s lighting fittings as required to finish the work for interior contractor necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules regulations as per Airport Security Department. The material shall be taken back by the contractor. | Job | 1 | 18500 | 18500
TOTAL FOR WIRING ACCESSORIES
VI | LIGHTING FITTINGS
Installation, testing commissioning of the following concealed surface mounted or suspended light fixtures AS PER FINAL APPROVAL FROM ARCHITECT CLIENT CONSULTANT with lamps, ballast all necessary mounting supporting accessories. No additional cost shall be paid for supporting.
1 | 600x600mm PANEL LIGHT | Nos. | 1 | 3800 | 3800
2 | SURFACE LIGHT | Nos. | 1 | 1000 | 1000
3 | PENDANT LIGHT-1 | Nos. | 4 | 4500 | 18000
4 | PENDANT LIGHT-2 | Nos. | 11 | 3200 | 35200
5 | COB LIGHT | Nos. | 5 | 1750 | 8750
6 | DECORATIVE WALL LIGHT | Nos. | 5 | 5200 | 26000
7 | LED STRIP LIGHT | Mtr. | 40 | 600 | 24000
8 | HOOD LIGHT | Nos. | 5 | 3200 | 16000
9 | 600x600mm PANEL LIGHT (Emg) | Nos. | 1 | 3800 | 3800
10 | PENDANT LIGHT-1 (Emg) | Nos. | 2 | 2700 | 5400
VII | EARTHING
1 | Supply and Installation of Maintenance Free Chemical earthing using Electrode of Size approx. 38 mm dia + - 2mm, 3 metres long bonded with 50x6 copper internal strip complete with excavation, civil works, cast iron cover with backfill compound min. 40 KG. The system shall be CPRI tested. Warranty period of chemical earthing from the date of commissioning shall be 5 years. Warranty implies the voltage between earth and neutral will not exceed 0 volts for earthing pits installed. (Note Body earthing provided by Base builder. We have considered Neutral earthing for UPS Server racks.)
3 | Supply erection of G.I. strip of 25 x 3 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | 60 | 175 | 10500
4 | 1 no. 4 sq. mm YY cable in 25mm GI conduit for earthing FOR NETWORK RACK | Mtr. | 45 | 135 | 6075
| Supplying erecting bare copper conductor of 8 swg for earthing purpose | Mtr. | 80 | 160 | 12800
VIII | MISCELLANEOUS
1 | Supply Installation of 6A 3 pin plug top | Nos. | 5 | 0 | 0
2 | Supply Installation of 16A 3 pin plug top | Nos. | 6 | 0 | 0
4 | Supply laying of Rubber Mats, CPRI tested conforming to standards like BS 921, ASTM-D 178 IEC 479 for different operatng voltage ratings as below.
| Supply of 2M x 1M Rubber mat suitable for operatng voltage upto 1.1 KV | Set | 1 | 4400 | 4400
5 | Supply fixing of approved shock treatment chart written in English and in local Language. The chart shall be framed in Teakwood and covered with glass. | Nos. | 1 | 5500 | 5500
7 | Supply fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language | Nos. | 1 | 500 | 500
9 | SITC of Emergency Exit signage (battery operated) approval by client architect consultant. Make Prolite or Equivalent | Nos.
A | DATA AND TELEPHONE SYSTEM
1 | Supply Installation of 25mm.dia. GI conduit with pull box junction box all accessories for DATA VOICE WIFI wiring as per the requirement. | Mtr. | 120 | 60 | 7200
2 | Providing DATA wiring inside 25mm dia GI conduit from each Data outlet to ICT CP Point by using Indoor Type CAT6A, | Mtr. | 200 | 55 | 11000
3 | Supply Installation of Internet Jack Unit RJ-45 suitable for CAT6A | Nos. | 8 | 300 | 2400
4 | Supply Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 3 Feet | Nos. | 8 | 850 | 6800
5 | Supply Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 7 Feet | Nos. | 8 | 1250 | 10000
6 | Supply laying indoors multi-pair 0.5mm dia copper PVC insulated and sheathed, armoured telephone cables on walls, ceiling, cable trays, trunking complete with clamps, cable markers etc. from MDF to the various tag blocks as specified
a | 10 pair cable armoured | Mtr. | 40 | 60 | 2400
7 | Supply installation of telephone tag block with KRONE terminal connectors, G.I.J.B as specified com-plete with all interconnections and jumper connections bet-ween the two tag blocks on all floors as shown on drgs.
b | 20 pair tel. tag block | Nos. | 1 | 750 | 750

## Plumbing Work
BOQ - Plumbing Work |  | PO |  |  |  | RA-01
S.N | ItemName | UOM | Quantity | Rate | Amount | Qty | Amount
A | WATER SUPPLY PIPING |  |  |  | 194260 |  | 132710
1 | CPVC Pipes conforming to ASTM D-2846, SDR-11 grade and CPVC solvent weld fittings like elbows, tees, couplars, brass threaded adaptors, insert ring etc. suitable for (domestic and flushing) cold applications rated, concealed piping within wall floor including jointing with fittings using solvent cement, brass threaded end fittings for making connection to fixtures. The work shall also include chasing the walls with machine wherever required for concealed piping and making good the same after laying of pipes necessary pressure testing Chasing finishing shall be done with 1 1 cement mixed mortar, restore the same original condition for internal and shaft piping, including necessary hot deep galvanised supports vertical horizontal, as per direction of Site incharge direction. [The rate shall include supply of S.S.screws and nut bolts etc.chasing in walls done by machine] (For Domestic and Flushing water-Toilet internal) (Pipe shall be tested with 1.5 times working pressure as covered in specifications)
1.1 | 20 mm Dia | R.mt | 40 | 75 | 3000 | 40 | 3000
1.2 | 25 mm Dia | R.mt | 10 | 90 | 900
1.3 | 32mm Dia | R.mt | 5 | 125 | 625
2 | Providing Fixing of gun metal heavy Ball Valves-PN-16 (approved makes as covered in specification) screwed type for water system of the following diameters. Valve shall have with unions.
2.2 | 25mm Dia | Nos. | 1 | 350 | 350
2.3 | 32mm Dia | Nos. | 1 | 450 | 450
3 | Providing ,fixing, testing and commissioning capstan make Water Meter including providing fixing matching Isolation valves ,strainer, non-return valve,complete with all necessary fittings etc screwed type(15Kgs Sq.cm). Valve shall have with union.
3.1 | 25 mm Dia incoming line | Nos. | 1 | 6000 | 6000 | 1 | 6000
4 | Supply, installation,testing commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG cm2 pressure, Wall Mounted Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories
4.1 | 20 L Capacity- | Nos. | 1 | 21500 | 21500 | 1 | 21500
6 | SITC of ACO grease trap -model Lipumobil S -Capacity -32 lit ( 0.5 LPS) with all required accessories ( Optional if not part of kitchen consultant Scope) | Nos | 1 | 35000 | 35000 | 1 | 35000
7 | SITC of SANICOM2 – Heavy Duty Duplex Drain Pump with all required accessories | Nos | 1 | 46485 | 46485
8 | RO PACKAGE PLANT-Supply , installations, testing and comminissioning of Package RO plant 100 Lit Hr including required pressure pumps panel pressurised tank if any , all assesories, valves and membrance cleaning system, ultra-violet sterilizer, internal piping, presure gages etc (System shall be Auto fill stop and Auto empty start mechanisam) | No | 1 | 27000 | 27000 | 1 | 27000
B | DRAINAGE
1 | uPVC-SWR pipes conforming to IS 13592 92 including fittings conforming to IS-14935 99 and agri type pipes above 100 mm dia. conforming to IS 4985, cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts supported on wall hung below slab etc. with all material labor complete and as directed. [The Rate shall include supply and fixing of hotdip galvanised bracket nut bolts PVC Coated U-Clamp and screws] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] (For Waste, Vent -Internal and vertical shaft ).
1.1 | 40mm Dia | R.mt | 5 | 150 | 750
1.2 | 50mm Dia | R.mt | 15 | 630 | 9450 | 15 | 9450
1.4 | 75mm Dia | R.mt | 20 | 810 | 16200 | 11 | 8910
1.5 | 100 mm Dia | R.mt | 5 | 940 | 4700
2 | Supply, Install PVC Floor Trap for the following pipes including making all approved quality Solvent cement joints with material labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 2 | 750 | 1500 | 2 | 1500
3 | Supply, Install PVC Multi Floor Trap for the following pipes including making all approved quality Solvent cement joints with material labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 1 | 850 | 850 | 1 | 850
D | S.S. GRATING
Only installations testing and commissioning of S.S.Gratings
2 | Making chamber in brick work including internal tiling etc for S.S Grating size, 350mm x 350mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing Site Engineer s instruction. | Nos. | 3 | 6500 | 19500 | 3 | 19500

## HVAC
HVAC work, AJ Kitchen- Ahmedbad |  |  | PO |  |  |  | RA-01
Sr No. | Item Code | Item Name | UOM | Quantity | Rate | Amount | Qty | Amount
|  | Total -HVAC Amount |  |  |  | 805029 |  | 165589.911
|  | High Side |  |  |  | 675689 |  | 103610.286
|  | Low Side |  |  |  | 129340 |  | 61979.625
1 |  | HVAC High Side work and Low side Work for AJ Kitchen Ahmedabad
2 | 1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT)
3 | 1.1 | CEILING SUSPENDED AHU
12 |  | Contractor shall design the chilled water coil according to the following conditions
13 |  | a. Coil air entering temperature - 75.4°F DB
14 |  | b. Coil air leaving temperature - 54 deg. F DB 52.99 deg. F WB
15 |  | c. Chilled water temperature entering - 6.0 deg. C 42.8 deg. F
16 |  | d. Chilled water temperature leaving - 13.3 deg. C 55.9 deg. F
17 |  | Make VTS Zeco Citizen
18 |  | Type Capacity Tonnage ESP No. of
19 |  | (Cfm) TR (mm WG) Rows
20 | a | CS AHU 1500 4.32 25 4 6 | No. | 1 | 118639 | 118639
29 | 2 | CHILLED WATER PIPING WITH INSULATION
30 | 2.1 | CHW PIPE
31 |  | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered.
32 |  | Make Jindal Hissar TATA
33 | a | F 32 mm | Rmt | 20 | 1500 | 30000
34 | 2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE
35 |  | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports.
36 |  | Make Armaflex K-flex
37 | a | F 32 mm | Rmt | 20 | 700 | 14000
38 | 2.3 | BALL VALVE
39 |  | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
40 |  | Make Zoloto Audco Kitz
41 | a | F 32 mm | Nos. | 3 | 2500 | 7500
42 | 2.4 | BALL VALVE WITH Y-STRAINER
43 |  | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation.
44 |  | Make Zoloto Audco Kitz
45 | a | F 32 mm | No. | 1 | 4800 | 4800
46 | 2.5 | PIBCV VALVES
47 |  | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
48 |  | Make Oventrop Siemens Danfoss
49 | a | F 32 mm | No. | 1 | 45000 | 45000
50 | 2.6 | Auto Air Vent Valves
51 |  | Make Anergy Flamco
52 |  | Providing and fitting Auto Vent Valves.
53 | a | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. | Nos. | 2 | 1500 | 3000
54 | 2.7 | SITC of Pressure gauges Thermometers
55 |  | Make H Guru Waree
56 |  | Necessary pressure gauges and thermometers 4 Dial type.
57 | a | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 | Nos. | 2 | 3500 | 7000
58 | b | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C | Nos. | 2 | 6000 | 12000
59 | c | Thermowells | Nos. | 4 | 4500 | 18000
61 | 2.8 | INSULATED CONDENSATE DRAIN PIPE
62 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
63 |  | Make Supreme, Prince, Astral
65 | b | F 32 mm | Rmt | 10 | 475 | 4750
73 |  | SUB-TOTAL |  |  |  | 264689 |  | 0
74 | 3 | VENTILATION SYSTEM
75 | 3.1 | KITCHEN DRY SCRUBBER
76 |  | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
80 |  | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
81 |  | Particle Size - Collects particles as small as 0.01 microns
82 |  | Motor - Sealead ball bearings UL, single phase.
83 |  | Cell - Ionizing voltage - 12 KVdc
84 |  | Collector voltage - 6 KVdc
85 |  | One cell comprising of 9 ionizing wires and 25 collection plates
86 |  | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
87 |  | Pre-filter - Aluminium mesh, washable Dry contact for BMS.
88 |  | Make Rydair Espair
89 |  | CFM - 3100 | No. | 1 | 210000 | 210000
90 |  | SUB-TOTAL |  |  |  | 210000 |  | 0
91 | 4 | SHEET METAL WORKS
92 | 4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
93 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
94 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat
95 |  | Make Rola Star, Zeco Ductofab
98 | c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 15 | 2100 | 31500
99 | d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 75 | 1404 | 105300 | 73.7965 | 103610.286
100 | 4.2 | EXTRUDED ALUMINIUM CEILING GRILLES
101 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. | Sq.mtr | 3 | 11700 | 35100
102 |  | Make Cosmos, Air Master System Air
103 | 4.3 | DOOR TRANSFER GRILLE
104 |  | SITC of Aluminium extruded powder coated Door transfer grills.
105 |  | Door transfer grille (Back to Back) | Sq.mtr | 1 | 13500 | 13500
106 |  | Make Cosmos, Air Master System Air
107 | 4.4 | EXTRUDED ALUMINIUM SQUARE AIR DIFFUSER
108 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air square diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect.
109 |  | Make Cosmos Ruskin Titus Air Master
110 | a | SQUARE DIFFUSER FOR GRID CEILING 600X600mm
111 |  | Supply Air Diffuser with OBD - Neck Size 225x225mm | Nos. | 1 | 2340 | 2340
112 | 4.5 | MULTI LEAF VOLUME CONTROL DAMPER
113 |  | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 1 | 5304 | 5304
114 |  | Make Cosmos, Air Master System Air
115 | 4.6 | OPPOSED BLADE DAMPER
116 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 1 | 4290 | 4290
117 | 4.7 | CANVAS CONNECTION
118 |  | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
119 | a | For AHU | No | 1 | 2496 | 2496
121 | 4.8 | CURTAIN TYPE FIRE DAMPER
122 |  | SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications.
123 |  | Make Carryaire System Air Dynacraft Air Master
125 | b | Fusible link as per specification UL 555 | No | 1 | 1170 | 1170
126 |  | NOTES
127 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
128 |  | Muslin cloth cover for all air outlets during construction.
129 |  | Pressure testing of complete duct work as per DW SMACNA standard.
130 |  | Silicon sealant for longitudinal transverse joints as per specification.
131 |  | Diffusers grilles shall be powder coated as per color approved by Architect.
132 |  | SUB-TOTAL |  |  |  | 201000 |  | 103610.286
133 | 5 | THERMAL ACOUSTIC INSULATION
134 | 5.1 | THERMAL INSULATION
135 |  | Supply fixing of Thermal insulation for supply air duct using 13mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 30 | 1000 | 30000 | 30 | 30000
136 |  | Make Armaflex K-flex
137 | 5.2 | ACOUSTIC INSULATION
138 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Sq.mtr | 5 | 1200 | 6000
139 |  | Make Armaflex K-flex
140 | 5.3 | THERMAL INSULATION FOR KITCHEN VENTILATION DUCTS
141 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 32 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. | Sq.mtr | 55 | 750 | 41250 | 42.6395 | 31979.625
142 |  | Make Armaflex K-flex
143 |  | Note
144 | a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
145 | b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
146 | c. | Thermal insulation shall be internal for Elliptical Expossed ducting.
147 |  | SUB-TOTAL |  |  |  | 77250 |  | 61979.625
148 | 6 | ELECTRICAL WORKS
149 | 6.1 | STARTER PANEL
150 |  | SITC of indoor outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Panel shall have provision to connect with BMS.
151 | a | Suitable for 1500 CFM AHU, DOL Starter Panel | No. | 1 | 28500 | 28500
152 | 6.2 | POWER CABLING
153 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
154 | a | Suitable Power Cable
155 |  | Suitable for 1500 CFM AHU, DOL Starter Panel | Rmt | 10 | 200 | 2000
156 | b | Earthing
157 |  | 8 SWG | Rmt | 20 | 125 | 2500
158 | 6.3 | BTU METER
159 |  | Supply,fixing and testing of inline Btu meter for the flow rate temperature measurement consisting mainly of following 3 parts
160 |  | a) Ultrasonic Flow Meter
161 |  | b) Matched pair of temp sensor
162 |  | c) Flowcell Sensor
163 |  | c) BTU Meter - 4 - 20mA DC from flowmeter
164 |  | Insertion type flowmeter shall be suitable for chilled water application for temp. Ranging from 0 to 50 deg C. Power supply shall be 240V AC (+ -) 15 %. Display shall have 16 characters LCD display with Back light, flow rate, Velocity, totaliser etc. Output shall be BMS Modbus compatible shall have keypad lockout security option. It also should be able to show various units such as gallons, ft^3, lbs, liters, m^3, kg etc
165 |  | Make Honeywell Danfoss Siemens
166 | a | Dia 32 mm | No. | 1 | 12580 | 12580
167 | 6.4 | CABLE TERMINATION
168 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor.
169 | a | Suitable for 1500 CFM AHU | No. | 1 | 3000 | 3000
170 | 6.5 | CABLE TRAYS
171 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports.
172 | a | 50mm wide x 50mm x 1.6mm Thick | Rmt | 10 | 351 | 3510
|  | SUB-TOTAL |  |  |  | 52090 |  | 0

## GAS
| AJ KITCHEN -AHMEDABAD AIRPORT | PO Qty |  |  |  | RA-01
BOQ FOR GAS PIPING SYSTEM- FDT |  |  |  | Rate | Amount | Qty | Amount
[5 empty] | 127145.8 |  | 34217.56
S/NO | DESCRIPTION | QUANTITY | UNIT
1 | Supply , instllation ,testing and commissioning of 32 NB CS seamless Sch. 40 pipe and fittings. Pipe conforming to ASTM A 106 Gr. B including required pipe supports | 12 | RMT | 1150 | 13800 | 4.3 | 4945
2 | Supply , instllation ,testing and commissioning of 25 NB CS seamless Sch. 40 pipe and fittings. Pipe conforming to ASTM A 106 Gr. B including required pipe supports | 12 | RMT | 1058 | 12696 |  | 0
3 | Supply of 32 NB L&T ball valve. Flanged end 150 # single pc design Fire Safe | 2 | No. | 4498.8 | 8997.6 | 1 | 4498.8
4 | Supply of 25 NB L&T ball valve. Screwed end, 3 pcs design | 2 | Nos. | 3376.4 | 6752.8 | 2 | 6752.8
5 | Painting of pipes. 2 coats of red oxide and 2 coats of Golden Yellow final paint. Total 120 microns thickness | 24 | RMT | 55.2 | 1324.8 | 4.3 | 237.36
6 | 2 mtrs long flexible Suraksha rubber hose for equipment connections | 2 | Nos. | 496.8 | 993.6 | 2 | 993.6
7 | 2nd Stage low pressure regulator for equipment connection. United works make | 2 | Nos. | 3220 | 6440 | 2 | 6440
8 | Pressure testing as per MGL requirement. Drawing for MGL and CFO submissions | 1 | JOB | 8280 | 8280 | 1 | 8280
9 | Installation, commissioning charges for all above including tranportation | 1 | JOB | 4140 | 4140 | 0.5 | 2070
| Sub - TOTAL |  |  |  | 63424.8 |  | 34217.56
Additional Items -
1 | LPG GAS LEAK DETECTOR | 2 | Nos | 12880 | 25760
2 | CONTROL PANNEL | 1 | Nos | 16675 | 16675
3 | 3 4 CORE X 4 SQCM COPPER FLEXIBLE | 12 | Mtr | 228 | 2736
4 | HOOTER | 1 | Nos | 1415 | 1415
5 | 4 VDC SOLONOID VALVE | 1 | Nos | 11960 | 11960
6 | NSTALLATION AND TESTING CHARGES WITH LABOUR | 1 | LS | 5175 | 5175
| Sub - TOTAL |  |  |  | 63721