## SUMMARY
Semolina Kitchens Pvt.Ltd.
Project : IDLI.COM HVAC
PO NO : | Semolina/PO/24-25/000083
Venodr Name : INVENTECH SOLUTIONS
SR NO | DISCRIPTION | PO VALUE | PREVIOUS BILL AMT (RA-1) | THIS BILL AMT (Final Bill) | CUMULATIVE AMT | VARIANCE AMT
1 | HVAC high side | 332920 | 332920 | 0 | 332920 | 0
2 | HVAC low side | 1002274 | 113384 | 387748 | 501132 | 501142
3 | Fire Sprinkler Work | 160540 | 0 | 96465 | 96465 | 64075
4 | Fire work | 157202 | 0 | 0 | 0 | 157202
| NET TOTAL | 1320016 | 446304 | 484213 | 930517 | 722419
| GST 18% | 237602.88 | 113626.72 | 69794.64 | 183421.36 | 130035.42
| GST 28% | 93217.6 |  | 17363.7 | 17363.7
| TOTAL | 1983756.48 | 559930.72 | 571371.34 | 1131302.06 | 852454.42

## HVAC high side
FOODCOURT AT AHMEDABAD AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
A | Part A: HVAC Equipments |  |  |  | 324220
B | Part B: Low Side Works
C | Part C: Electrical Works
TOTAL |  |  |  |  | 324220
GST @ 18% |  |  |  |  | 58359.6
GRAND TOTAL |  |  |  |  | 382579.6
FOODCOURT AT AHMEDABAD AIRPORT
SCHEDULE OF PRICES - HVAC WORKS
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.) | Actul Qty | Amount
Part A | HVAC Equipments
1 | Air Handling Units (Indoor Type)
Supply , Installation , testing & commissioning Of Double skin Floor mounted / Ceiling Suspended Type air handling units of extruded aluminium section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG/m3 , with Plug Fans / Backward Type DIDW Blower with TEFC motors, copper cooling coils as mentioned below , with aluminium fins, MERV-8 and MERV 13 Filters. The drain pan shall be constructed out of 18G stainless steel duly insulated. All the AHU's installed under this tender shall have minimum IE2 motor or better. All the cooling coils shall be AHRI / Eurovent Certified . The AHU Coil shall be selected at 9 deg C Chilled water Inlet Temp Temperature. Approval of AHU Technical Data by consultant prior to fabrication is required. The cost of AHU shall be inclusive of factory fitted VFD of approved make.
Design Parameters- 25 deg C -R.A.Temp, 55% RH, 9 deg C- CHW IN
Water Flow Rate- 2.0 GPM/ TR
1.1 | Ceiling Suspended Type
1.1.1 | 6800 CMH(4000 CFM)at 25 mm External Static Pressure, 6 RD Cooling Coil, Approx 8 TR, 1 x 2.25 KW Motor | Nos | 1 | 324220 | 324220 | 1 | 324220
1.2 | Digital Heating/Cooling Thermostat for Air Handling Units | Nos. |  | 8700 | 0 | 1 | 8700
Sub Total Part A |  |  |  |  | 324220 |  | 332920

## HVAC Low side
FOODCOURT AT AHMEDABAD AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
A | Part A: HVAC Equipments
B | Part B: Low Side Works |  |  |  | 912811
C | Part C: Electrical Works |  |  |  | 18960
TOTAL |  |  |  |  | 931771
GST @ 18% |  |  |  |  | 167718.78
GRAND TOTAL |  |  |  |  | 1099489.78
FOODCOURT AT AHMEDABAD AIRPORT
SCHEDULE OF PRICES - HVAC WORKS
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract. | [5 empty] | Previous Bill |  | Final Bill
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.) | Actul qty. | Amount | Actul qty. | Amount
Part B | Low Side Works
1 | Chilled Water Piping with Nitrile Rubber Insulation
Supplying, laying/ fixing, testing and commissioning of MS C class chilled water piping (cut of required length and installed with welded joints. The necessary fittings such as elboues, tees etc. shall all to included in this item). The Insulation shall be Class O nitrile Rubber pre-slit, pipe sleeve upto 100 mm dia and sheet for bigger dia with factory Laminated 7 mill woven glass cloth of thicknesses as specified, with approved adhesive. Manufactured supplied, suitable sized nitrile rubber pipe supports with PUF/PIR inserts shall be used. Thermal conductivity should not exceed 0.035 W/MK at 0 degree celsius and water vaper resisitance > 7000. Manufactures tapes and adhesive to used only. The pipe supports should also be of nitrile rubber with PUF/PIR inserts and are to be installed as per manufacturer's recomendation. The pipe fittings shall be MS. class for pipes upto 150 mm and for 200mm and above, same material of the pipe shall be usee all bends/ Reducess/ Tee upto 150 mm shall be factory fabricated ready made MS 'C' class. Note : Use proper template for marking block colour Arrows pipe. for supply/return.
I | 40mm dia with 32 mm thick insulation with factory Laminated 7 mil glass cloth upper layer | Mtrs. | 20 | 1724 | 34480 | 20 | 34480
2 | Insulated Valves
2.1 | Dynamic Balancing Valve-PID type
Supply & installation, testing and commissioning of BMS Compatible electronic self balancing valve with integrated two way modulating control valves in a single body. The actuator shall be capable of accepting 230V/ 24V/ 2-10VDC/4-20 mA electrical signed and shall provided similar transduced feed back output singed to control system. The minimum close off pressure of actuator must be 1.5 times shut of head of pump as per Specification of following size. The actuator shall be microprocessor based with self calibration feature. All the valve shall be complete with step down transformers, thermostat, control wiring and probe.
i. | 10-30 USGPM Insulation as per pipes | Nos. | 1 | 44844 | 44844 | 1 | 44844
2.2 | Manual Butterfly Valves (Insulated)
Providing and Fixing of the following valves with PN-16 Ratings complete with flanges /nuts/ bolts/gaskets etc. Butterfly valve shall have CI body seal of black nitrile rubber (tight shutoff) S.G. iron disc(nylon coated) PTFE coated shafts etc. as required. These valves should be suitable for flow in either direction and seal in both directions and should be integral moulded design.
2.2.1 | 40 mm dia -PN16 -- Insulation as per Chilled water pipe | Nos. | 2 | 6699 | 13398 | 2 | 13398
2.3 | Y- Strainer (Insulated)
Providing and Fixing of the insulated Y-Strainer fabricated out of MS with removable bronze screen, 3mm perforation and permanent magnet etc. complete in all respect and as per specifications and drawings.
2.3.1 | 40 mm dia -PN16 -- Insulation as per Chilled water pipe | Nos. | 1 | 7273 | 7273 | 1 | 7273
2.4 | Providing and Fixing digital type thermometers with copper well, valve & probe suitable for binder test point application.
2.4.1 | 12" long (Insulated) | Nos. | 2 | 2540 | 5080 | 1 | 2540
2.5 | Dial Presure Guages (glycerine filled Type) with SS Encasing with isolating valve & piping etc.The gauge should be with appropriate range and valve and fitted with probe suitable for binder test point application as well.
2.5.1 | 6" Dial (Insulated) | Nos. | 2 | 3770 | 7540 | 2 | 7540
2.6 | Providing and Fixing of automatic air vent of approved make with insulation valves as per specifications/drawings
2.6.1 | 20mm dia | Nos. | 1 | 2621 | 2621 | 1 | 2621
3 | Drain Piping
Supply, Installation, testing and commissioning of UPVC condensate drain pipe along with necessary clamps, fittings sich as bends, tees, etc. it shall be insulated with 9 mm thick nitrile foam insulation in tubular form as per specifications.
3.1 | 25 mm dia | Mtrs. | 4 | 172 | 688 | 4 | 688
4 | DUCTING
4.1 | G.I. Sheet Metal Ducting - Factory Fabricated
Installation, Testing and Commissioning of factory fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
4.1.1 | 0.50 MM (26 Gauge) | Sqm. | 20 | 1314 | 26280
4.1.2 | 0.63 MM (24 Gauge) | Sqm. | 40 | 1406 | 56240
4.1.3 | 0.80 MM (22 Gauge) | Sqm. | 15 | 1578 | 23670
4.1.4 | 1.00 MM (20 Gauge) | Sqm. | 5 | 1867 | 9335
4.1.6 | 1.00 MM (20 Gauge)- Kitchen Exhaust Ducting with 25 mm thick high density of glasswool / rockwool insulation of density 48kg/m3 . The insulation shall be covered with muslin cloth over which 2 coats of Starbond / approved fire paint is applied to make the insulation hard and fire retardant . | Sqm. | 70 | 2800 | 196000
4.2 | G.I. Sheet Metal Ducting - Site Fabricated
Installation, Testing and Commissioning of site fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
4.2.1 | 0.63 MM (24 Gauge) | Sqm. | 10 | 1107 | 11070 |  |  | 10 | 11070
4.2.2 | 0.80 MM (22 Gauge) | Sqm. | 5 | 1295 | 6475 |  |  | 5 | 6475
4.2.3 | 1.00 MM (20 Gauge) | Sqm. | 5 | 1523 | 7615 |  |  | 5 | 7615
5 | INSULATION
5.1 | Nitrile Rubber Insulation- Class 'O'
Supplying and fixing of closed cell elastomeric insulation of density 55 kg/cu.m.and K valueof not less than 0.037W/mk at 20 deg C as per specifications and drawings (For indoor applications) with factory Laminated 7 mill woven glass cloth
5.1.1 | 19 mm thick (AC ducts / Fresh Air Duct) | Sqm. | 95 | 746 | 70870 |  |  | 20 | 14920
5.2 | Acoustic Lining
Supplying and Application of Acoustic lining within the Supply Air duct with 15 mm thick class 'O' open cell nitrile Rubber of density 140-160 kg./Cubm. as per spefications.
5.2.1 | 15 MM Thick | Sqm | 10 | 1514 | 15140
6 | DUCT ACCESSORIES
6.1 | Supply, Installation, Testing and Commissioning of GI multiblade volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 3 | 7581 | 22743 |  |  | 3 | 22743
6.2 | Supply, Installation, Testing and Commissioning of multiblade Al volume control Collar / Grille / exhaust Air Opening damper complete with suitable links, lever and quadrants for manual control of airflow and with suitable links , lever and quadrants for manual control of airflow and neoprene rubber gaskets, nuts, bolts, screws, flanges etc., as per specifications. | Sqm. | 3 | 11394 | 34182 |  |  | 3 | 34182
6.3 | Supply, Installation, Testing and Commissioning & fixing of powder coated extruded aluminium Supply / Exhaust Air Grills as per specifications | Sqm. | 2 | 6854 | 13708 |  |  | 2 | 13708
6.6 | Supply, Installation, Testing and Commissioning & fixing of powder coated extruded Aluminium Continuous Grille as per specifications
6.6.2 | 150 MM Aluminium Continuos Grille | RM | 15 | 6850 | 102750 |  |  | 14 | 95900
6.6.3 | 100 MM Aluminium Continuos Grille | RM | 30 | 6355 | 190650 |  |  | 15 | 95325
11 | Louvers
11.1 | Providing and fixing of powder coated extruded aluminium exhaust air louvers/ fresh air louvers with bird screen and mounting arrangement as per specification and drawings. Free Area shall be more than 60% of gross area.
11.1.1 | Fresh Air / Exhaust Air Louvers with Bird Screen Mesh | Sqm. | 1 | 10159 | 10159
Sub Total Part B |  |  |  |  | 912811 |  | 113384 |  | 301938
Part C | Electrical Works
1 | Electrical Control Panel
Supply, installation, testing and commissioning of panel boards made of 2.0 mm thick steel sheet duly powder coated with voltmeter, ammeter, electronic energy meter, indicating lights, Stop/manual /Auto selector switch in each, outgoing current operated single phase preventer. The starters should have potential free contacts for connection to Building Automation System. The panel shall include contactors /over load relay with built in single phase protection / Time delay relay for delayed automatic start of the motor. All panels should have spare NO/ NC Contacts for BMS applications as required.
1.1 | Panel-PA01
(1 x 2.25 KW)
OUTGOING
1 No. 16 Amps TP MCB for AHU's
1 No. DOL starter for 2.25 KW motor .
1 No. of single phase preventor (current based-MPRD2)
1 No. direct reading Digital Type Ammeter
| Each star-delta/DOL starter consists of current operated MN type over load relay, contactor, push button, ON/OFF indication light | Set |  | 66850 | 0 |  |  | 1 | 66850
2 | Cables
Supplying, laying, testing and commissioning of XLPE insulated aluminium conductor armored cables of 1.1 KV grade of following sizes directly on wall/structural frame/ cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends, double earthing with GI strip/wire of suitable size and hardware as per specifications.
i. | 3 C x 4 Sq. mm | Mtrs | 25 | 378 | 9450 |  |  | 25 | 9450
2.1 | Cabling(Copper)
i. | 2C x 1.5 sqmm | Mtrs | 10 | 183 | 1830 |  |  | 10 | 1830
3 | Earthing
Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts/ in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043:1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required
3.1 | 25 mm x 3 mm GI strip | RM | 10 | 495 | 4950 |  |  | 10 | 4950
3.2 | 8 SWG GI Wire | RM | 10 | 273 | 2730 |  |  | 10 | 2730
Sub Total Part C |  |  |  |  | 18960 |  |  |  | 85810
Total

## Fire Sprinkler Work
BILL OF QUANTITIES FOR SPRINKLER WORK LOCATION:- Ahemdabad Food Court
SR. NO. | DESCRIPTION | UNIT | PO QTY. | RATE | AMOUNT | Remarks
1 | Providing, Laying, Jointing & Testing of Pipes for Sprinkler System - G.I Pipe confirming IS Codes Class `C' Heavy Pipe & with necessary support & anchore fastening from slab.
a. | 25 mm dia | Rft. | 115 | 250 | 28750
c. | 40 mm dia | Rft. | 60 | 350 | 21000
d. | 50 mm dia | Rft. | 10 | 450 | 4500
2 | Synthetic Enamel Paint.
a. | 25 mm dia | Rft. | 120 | 27 | 3240
c. | 40 mm dia | Rft. | 60 | 27 | 25
d. | 50 mm dia | Rft. | 10 | 27 | 270
3 | Providing & Fixing of Butterfly Valve.
a. | 40 mm dia | No. | 2 | 4500 | 9000
b. | 50 mm dia | No. | 1 | 5200 | 5200
7 | Providing & Fixing C.P. Brass 79 degree(QR) Quartzoid Bulb Sprinklers. Make : Tyco / viking temp rating standard coverage discharge coefficent k- 6.6 quick response UL listed & EN approved for high temperature area in Kitchen temprating shall be 79degree c (QR)
a. | Pendant Type | No. | 12 | 1200 | 14400
8 | Flexible Sprinkler Drop.
a. | 25mm | No. | 12 | 840 | 10080
Total |  |  |  |  | 96465