## BOQ Price Bid
Addressable Fire Alarm System
BOQ for FAS for Delhi T1- Subway |  |  |  | AS PER WO |  |  | RA-1 BILL
Sr No. | Item Name | Item Description | UNIT | Qty | RATE | Amount | % | AMOUNT
1 | 9954 | Supply, Installation, Testing and Commissioning of addressable manual call point to monitor and signal to the control and indicating equipment the status of a switch operated by a resettable/deforamable assembly be capable of operating by means of thumb pressure and not require a hammer. Incorporate a mechanism to interrupt the normal addressable loop scan to provide an alarm re-sponse within less than 3 seconds. Capable of being tested using a special 'key' without the need for depressing the unit. Provide an integral red LED to indicate activation. Call point to include the use of a yellow led to signal fault condition also to have integral isolator. | NOS | 2 | 7910 | 15820 | 75% | 11865
2 | 9954 | Supply, Installation, Testing and Commissioning of Intelligent Addressable Optical Smoke detector with base. Detector shall have a configuration mode that gives separate alarms. | NOS | 14 | 5640 | 78960 | 75% | 59220
3 | 9954 | Supply, Installation, Testing and Commissioning of addressable loop powered sounder with strobe and incorporate an integral line isolator. Be capable of producing a sound output of 103dB at 1m. 16 selectable tones which can be configured using panel configuration software.Hooter shall stop at alarm "Acknowledge" and the Strobe shall stop at panel "Reset" | NOS | 2 | 7590 | 15180 | 75% | 11385
4 | 9954 | Supply, Installation, Testing and Commissioning of response indicator for above ceiling existing detectors | NOS | 7 | 750 | 5250 | 75% | 3937.5
5 | 9954 | Programming of the entire system into the exisiting panel with airport system. The rate shall also include supply and installation of Control module , Monitor module etc as required for zone integration | NOS | 1 | 40000 | 40000 | 75% | 30000
6 |  | Supply, Laying, Commissioning testing of 2c x 1.5 sqmm CU AR. PVC insulated, and overall PVC sheathed cable ; FR ,laid on wall ceiling using GI clamps and spacers as per the route decided at site, by looping all smoke detectors as required including | MTR | 150 | 120 | 18000 | 75% | 13500
|  | TOTAL AMOUNT |  |  |  | 173210 |  | 129907.5
|  | GST |  |  | 18% | 31177.8 |  | 23383.35
|  | GRAND TOTAL WITH GST |  |  |  | 204387.8 |  | 153290.85
| CERTIFIED BY NAME:….................................. | CERTIFIED BY NAME:….................................. | DATE:…................................ |  |  | Sign..................................