## PI
VART
Infracon Pvt Ltd
229, Neha Ind. Est., Off Duttapada Road,
Opp. Oberoi Sky, Borivali (E), Mumbai - 400066
Contact No :- 022-40233596 / 28700110 Email : info@vartinfra.com
Proforma Invoice
To, | Simolina Kitchen Pvt. Ltd. | Date |  | 2024-10-18
Ra-5th
Kindly Attn.:- Irfaan ji
Sr. No. | Description | Unit | QTY | Rate | Amount
1 | The Irish House Mep work | Job | 1 | 160295 | 160295
|  |  |  | Basic Total | 160295
|  |  |  | Add GST @ 18% | 28853.1
|  |  |  | Grand Total | 189148.1
Work Completion Time Period
Material Delivery 1o days from the Date of PO with advance
Payment terms :
100% Advance with Work order
No Retention
For VART Infracon Pvt. Ltd.
Authorised Signatory

## SUMMARY
PRICE COMPRTIVE - MEP @ IRISH HOUSE @ LUCKNOW RA-5th
Sr. No. |  | Amount in Boq | Amount |  |  |  | Remarks
|  |  | Previous Bill | This Bill | Up TO Date | Varation
1 | Electrical | 1148285 | 851370 | 160295 | 1011665 | 136620
2 | PHE | 153430 | 103596.1 | 0 | 103596.1 | 49833.9
3 | HVAC | 799245 | 415715.2 | 0 | 415715.2 | 383529.8
4 | Fire Fighting | 155465 | 151522.9 | 0 | 151522.9 | 3942.1
5 | Fire Alarm | 92300 | 72500 | 0 | 72500 | 19800
6 | CCTV | 149675 | 124695 | 0 | 124695 | 24980
7 | PA System | 125550 | 12058.5 | 0 | 12058.5 | 113491.5
| TOTAL | 2623950 | 1731457.7 | 160295 | 1891752.7 | 732197.3
2043120.086

## Electrical
The Irish House @ LUCKNOW
ELECTRICAL BOQ
SR. No | DESCRIPTION | UOM | QTY | Rate |  | Qty. |  |  | Amount in Rs. |  |  |  | Remarks
[5 empty] | Amount | Previous Bill | This Bill | Up To Date | Previous Bill | This Bill | Up To Date | Varation
I | PANEL & SWITCHGEAR
1 | Supply, installation, testing & commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process and duly powder coated using Siemens Grey Shade No. RAL 7032. The frame structure, doors and gland plates shall have 2.0 mm thick sheets and partitions shall be with 1.6 mm thick CRCA sheet. Base channel size 75 x 40 x 6 mm of ISMC shall be provided. The panel shall be dust and vermin proof with neoprene gasket. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus bar shall be of tinned Copper with epoxy supports and shall be insulated with colour coded heat shrink sleeves. The control wiring min. 2,5 Sq.mm shall be ZHLS type. The Panel shall be provided with CTs, phase indication lamps, meters, relays and all switchgear, etc. as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant. All componants for Switchgears shall be L&T/Legrand
a | Providing & installing MAIN LT PANEL as per SLD & Spec.: | Set | 1 | 70000 | 70000 | 1 | 0 | 1 | 70000 | 0 | 70000 | 0
63 Amps 4 pole, 16kA MCCB with Microprocessor Based overload, short circuit & Earth Fault protection, Energy manager (EM6400NG) with RS485 port for BMS connectivity & 4A with SP MCB with 100/5A-3 Nos., 15VA, CL-1 CT's for metering & of AE make and phase indicating lamps Vaishno make with SPMCB. CBCT with microprocesor based EFR
Busbar chamber - 1 set, 4 pole 100A Tinned Cu. Busbar with necessary
OUTGOINGS:
i. | 63A 4P MCB – 1 Nos.
ii. | 40A 4P MCB – 2 Nos.
iii. | 40A DP MCB – 2 Nos.
iv. | MPCB suitable for 2.2kW-2 Nos.
2 | Supply, installation, testing & commissioning of Switchgears.(Standard Product)
a | Supply,Installation,Testing and Commissioning of 40 Amps,4Pole MCB with ELCB at 300mAh for HVAC Outdoor Isolation all complete with mounting accessories | Nos. | RO
b | Supply,Installation,Testing and Commissioning of 32 Amps,4Pole MCB for HVAC Outdoor Isolation all complete with mounting accessories. | Nos. | 2 | 3250 | 6500 | [6 empty] | 6500
c | Supply,Installation,Testing and Commissioning of 40 Amps, DP, MCB for UPS/INVERTER Isolation all complete with mounting accessories for UPS. | Nos. | 2 | 2000 | 4000 | 2 | 0 | 2 | 4000 | 0 | 4000 | 0
d | Supply & installation of DOL starter L&T/Siemens/Legrand for 3 kW load | Nos. | RO
e | Supply & installation of DOL starter L&T/Siemens/Legrand for 4 kW load | Nos. | RO
f | Supply & installation of Star Delta starter as per Type-2 Coordination for 3 kW (4HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Exhaust air fan)(EXISTING UNIT PROVIDED BY MALL) | Nos. | RO
g | Supply & installation of Star Delta starter as per Type-2 Coordination for 9.3 kW (12.5HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Exhaust air fan) | Nos. | RO
h | Supply & installation of Star delta starter as per Type-2 Coordination for 5.5 kW (7.5HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Fresh air fan) | Nos. | RO
i | Supply & installation of DOL starter as per Type-2 Coordination for 2.2 kW (3.0HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For AHU) | Nos. | RO
j | Supply & installation of DOL starter as per Type-2 Coordination for 1.5 kW (2.0HP) pump load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Scrubber) | Nos. | RO
k | 80 amps 4P ELMCB 300mA with 63A 5 Pin Ray Roll Socket complete with all mounting accessories – for Indoor Legrand make model No. 6078 80 | Nos. | RO
l | 63 amps 4P ELMCB 300mA with 63A 5 Pin Ray Roll Socket complete with all mounting accessories – for Indoor Legrand make model No. 6078 80 | Nos. | RO
m | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make model No. 6078 80 | Nos. | RO
n | 25 amps 4P MCB with 25A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make model No. 6078 80 | Nos. | RO
o | 25A Rey roll socket complete with 25 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | Nos. | RO
p | 20A Rey roll socket complete with 32 amps DPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | Nos. | 1 | 2300 | 2300 | [6 empty] | 2300
q | 5/15A Rey roll socket complete with 15 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | Nos. | 7 | 2000 | 14000 | [6 empty] | 14000
r | Set of 1no 25A Metal clad Socket with MCB, and 2nos 6/16A Switch sockets housed in Fabricated SS Panel suitable for hanging arrangement for Kitchen equipments. | Nos. | RO | [8 empty] | 0
q | 5/15A Swicth socket complete (IP-65) for Kitchen | Nos. | 20 | 3200 | 64000 | 10 | 0 | 10 | 32000 | 0 | 32000 | 32000
3 | SITC of Standalone Gas leak detector with inbuilt sounder for Kitchen | Nos. | RO | [8 empty] | 0
0
| TOTAL FOR MAIN PANEL & SWITCHGEAR | [10 empty] | 0
0
II | INVERTER / UPS | [10 empty] | 0
0
1 | Supply, Installation, testing and commissioning of 6 KVA UPS System Single Phase I/C & Single Phase O/G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings & the specifications. | Nos | 1 | 52000 | 52000 | 1 | 0 | 1 | 52000 | 0 | 52000 | 0
0
| TOTAL FOR UPS | [10 empty] | 0
0
III' | DISTRIBUTION BOARDS | [10 empty] | 0
| Supply, installation, testing & commissioning of Distribution Boards surface / flush mounted with Double door containing MCB/ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs/RCCB should be of 30mA/100 mA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be 'D' type and other MCBs shall be 'C' category for lighting and raw power DB LEGRAND/L&T | [10 empty] | 0
0
1 | Lighting Distribution Board - LPDB | Nos. | 1 | 29000 | 29000 | 1 | 0 | 1 | 29000 | 0 | 29000 | 0
| 12 WAY TPN DB | [10 empty] | 0
| I/C- 1 # 40A FP MCB , 16KA | [10 empty] | 0
| SUB I/C - 3 # 25A DP RCCB 30mA per phase | [10 empty] | 0
| O/G - 30 # 10/20A SP MCB | [10 empty] | 0
0
2 | RAW Power Distribution Board - RPDB | Nos. | RO | [8 empty] | 0
| 6(8) WAY TPN DB | [10 empty] | 0
| I/C- 1 #40 A FP MCB | [10 empty] | 0
| SUB I/C- 3#40 DP ELCB 300mA per ph | [10 empty] | 0
| O/G - 18 # 16/20A SP MCB | [10 empty] | 0
0
3 | Kitchen Power DB - (KPDB-1) | Nos. | 2 | 24500 | 49000 | 1 | 0 | 1 | 24500 | 0 | 24500 | 24500
| 8 WAY TPN DB | [10 empty] | 0
| I/C- 1 #40 A FP MCB | [10 empty] | 0
| SUB I/C- 3#32 DP ELCB 100mA per ph | [10 empty] | 0
| O/G - 18 # 16/20A SP MCB | [10 empty] | 0
0
4 | EMERGENCY LIGHTING DB (ELDB/UPSDB) | Nos. | 1 | 13000 | 13000 | 1 | 0 | 1 | 13000 | 0 | 13000 | 0
| 12 way SPN DB | [10 empty] | 0
| Incomer: 40A DP RCBO 30mA | [10 empty] | 0
| Outgoings :10/16 SP MCB, 'D' Type – 8 Nos | [10 empty] | 0
0
| TOTAL FOR DISTRIBUTION BOARDS | [10 empty] | 0
0
IV | CABLES & ACCESSORIES | [10 empty] | 0
| Supply & installation of following LT XLPE FRLSH cables (FINOLEX/RR KABLE/POLYCAB) rated for 600 / 1100 volts AC as per IS standard 1554 Part 1 with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20 mtrs and ten finally with metal identification tags showing the size and the location from/to the specific Panel/DB at both ends. | [10 empty] | 0
1 | 3.5C x 300 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
2 | 3.5C x 240 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
3 | 3.5C x 185 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
4 | 3.5C x 150 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
5 | 3.5C x 120 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
6 | 3.5C x 95 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
7 | 3.5C x 70 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
8 | 3.5C x 50 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
9 | 3.5C x 35 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
10 | 4C x 16 Sq. mm A2XFY | Mtr. | 100 | 243 | 24300 | [6 empty] | 24300
11 | 4C x 10 Sq. mm A2XFY | Mtr. | RO | [8 empty] | 0
12 | 4C x 10 Sq. mm 2XFY ( Cu ) | Mtr. | RO | [8 empty] | 0
13 | 4C x 16 Sq. mm 2XFY ( Cu ) | Mtr. | RO | [8 empty] | 0
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 30 | 400 | 12000 | 3 | 5 | 8 | 1200 | 2000 | 3200 | 8800
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 60 | 400 | 24000 | [6 empty] | 24000
16 | 4C x 2.5 Sq. mm 2XFY Cable ( Cu ) | Mtr. | RO | [8 empty] | 0
17 | 3C x 6sq. mm YWY cable ( Cu ) | Mtr. | 20 | 350 | 7000 |  | 16 | 16 |  | 5600 | 5600 | 1400
18 | 3C x 4sq. mm YWY cable ( Cu ) | Mtr. | 40 | 350 | 14000 |  | 8 | 8 |  | 2800 | 2800 | 11200
19 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | Mtr. | RO | [8 empty] | 0
20 | 1C x 10 Sq. mm YY cable ( Cu ) | Mtr. | RO | [8 empty] | 0
21 | 1C x 6 Sq. mm YY cable ( Cu ) | Mtr. | RO | [8 empty] | 0
22 | 1C x 4 Sq. mm YY cable ( Cu ) | Mtr. | RO | [8 empty] | 0
23 | 5Rx1Cx16 Sq.mm YY FRLS Cable (Cu) | Mtr. | RO | [8 empty] | 0
24 | 5Rx1Cx10 Sq.mm YY FRLS Cable (Cu) | Mtr. | RO | [8 empty] | 0
25 | 5Rx1Cx6 Sq.mm YY FRLS Cable (Cu) | Mtr. | RO | [8 empty] | 0
26 | 5Rx1Cx4 Sq.mm YY FRLS Cable (Cu) | Mtr. | RO | [8 empty] | 0
0
B | Termination of following sizes of cables with Single compression cable gland.(COMET/BRAKO) | [10 empty] | 0
0
1 | 3.5C x 300 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
2 | 3.5C x 240 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
3 | 3.5C x 185 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
4 | 3.5C x 150 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
5 | 3.5C x 120 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
6 | 3.5C x 95 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
7 | 3.5C x 70 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
8 | 3.5C x 50 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
9 | 3.5C x 35 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
10 | 4C x 16 Sq. mm A2XFY | Nos. | 2 | 650 | 1300 |  | 1 | 1 |  | 650 | 650 | 650
11 | 4C x 10 Sq. mm A2XFY | Nos. | RO | [8 empty] | 0
12 | 4C x 10 Sq. mm 2XFY ( Cu ) | Nos. | RO | [8 empty] | 0
13 | 4C x 16 Sq. mm 2XFY ( Cu ) | Nos. | RO | [8 empty] | 0
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | Nos. | 6 | 550 | 3300 |  | 3 | 3 |  | 1650 | 1650 | 1650
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) | Nos. | 4 | 500 | 2000 | [6 empty] | 2000
16 | 4C x 2.5 Sq. mm 2XFY Cable ( Cu ) | Nos. | RO | [8 empty] | 0
17 | 3C x 6sq. mm YWY cable ( Cu ) | Nos. | 4 | 500 | 2000 | [6 empty] | 2000
18 | 3C x 4sq. mm YWY cable ( Cu ) | Nos. | 4 | 400 | 1600 | [6 empty] | 1600
19 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | Nos. | RO | [8 empty] | 0
20 | 1C x 10 Sq. mm YY cable ( Cu ) | Nos. | RO | [8 empty] | 0
21 | 1C x 6 Sq. mm YY cable ( Cu ) | Nos. | RO | [8 empty] | 0
22 | 1C x 4 Sq. mm YY cable ( Cu ) | Nos. | RO | [8 empty] | 0
23 | 5Rx1Cx16 Sq.mm YY FRLS Cable (Cu) | Nos. | RO | [8 empty] | 0
24 | 5Rx1Cx10 Sq.mm YY FRLS Cable (Cu) | Nos. | RO | [8 empty] | 0
25 | 5Rx1Cx6 Sq.mm YY FRLS Cable (Cu) | Nos. | RO | [8 empty] | 0
26 | 5Rx1Cx4 Sq.mm YY FRLS Cable (Cu) | Nos. | RO | [8 empty] | 0
0
| TOTAL FOR CABLES & ACCESSORIES | [10 empty] | 0
0
V | WIRING & ACCESSORIES | [10 empty] | 0
0
| Notes : | [10 empty] | 0
0
| 1) Rates for point wiring shall include supply & installation of Wires & wiring acccessories such as angle holders/ceiling roses as required. conduits, conduit accessories such as junction boxes, Ts, elbows etc,Switches, sockets & fixtures shall not be included in the point wiring rates. These will be counted & paid separately. | [10 empty] | 0
0
| 2) Unless otherwise specified, all wires in point wiring shall be 2.5 sq.mm | [10 empty] | 0
| Stranded copper conductor 1.1 KV grade, I.S.I. marked (P+N+E), | [10 empty] | 0
| LSZH) PVC insulated . | [10 empty] | 0
| Wires shall be colour coded (Red, Yellow and Blue for Phases, | [10 empty] | 0
| Black for Neutral & Green for earth). | [10 empty] | 0
0
| 3) Looping of wires shall be in fittings and switch boxes only | [10 empty] | 0
0
| 4) Location of switches/sockets/ DBs shown on the drawings shall | [10 empty] | 0
| be confirmed with the Architect/ Consultant/ Project Manager | [10 empty] | 0
| before installation. | [10 empty] | 0
0
| 5) All Surface and concealed Conduits shall be rigid GI conduits of | [10 empty] | 0
| size not less than 20 mm dia as per applicable IS. | [10 empty] | 0
0
| 6)The Contractor can take more than one circuit in the same conduit | [10 empty] | 0
| provided they are of the same phase. The size of conduit shall be | [10 empty] | 0
| decided according to the number of wires in it as per applicable IS & as | [10 empty] | 0
| specified. | [10 empty] | 0
0
| 7) Payments for light fixtures & fans will be made separately as per the | [10 empty] | 0
| items given in 'Light Fixtures & Accessories'. | [10 empty] | 0
0
| 8) Type & location of light fixtures shown in the drawings are | [10 empty] | 0
| tentative and subject to revision as per the recommendation of | [10 empty] | 0
| Architect/ Consultant. The quantities (number of points and accessories) | [10 empty] | 0
| of point wiring will be revised as actual installed on account of such | [10 empty] | 0
| revisions in the layouts. | [10 empty] | 0
0
| 9) Circuit wiring from DBs to the switch boards or first light point shall | [10 empty] | 0
| Be included as primary points & remaining points of the same looping | [10 empty] | 0
| shall be considered as Secondary points and shall be counted in nos. | [10 empty] | 0
0
| 10) Circuit Wiring from DB to Kitchen Power points shall be measured in running meters | [10 empty] | 0
0
0
1 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included. | [10 empty] | 0
| Averagepoint length of primary&secondaryto be derived by Contractor, fromthe drawing provided AND+/-1MtrMeasured Radially | [10 empty] | 0
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | Nos. | 20 | 1760 | 35200 | 21 | 0 | 21 | 36960 | 0 | 36960 | -1760
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | Nos. | 90 | 1050 | 94500 | 98 | 32 | 130 | 102900 | 33600 | 136500 | -42000
0
2 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Switch Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same switch board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI. conduits, 6A switch & switch board and accessories shall be included. | [10 empty] | 0
a) | Primary Light points controlled by Switch (3R x 2.5 sqmm wire) | Nos. | 1 | 1760 | 1760 | 1 | 0 | 1 | 1760 | 0 | 1760 | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | Nos. | 2 | 1050 | 2100 | 2 | 0 | 2 | 2100 | 0 | 2100 | 0
c) | DB to SB & SB to SB circuit wiring : For Switch Operated Primary point @ SB to SB loop point. Wiring for switch board controlled by MCB already installed in DB by using 3 X 2.5 sq. mm flexible LSZH copper wires in 25mm GI conduits as per IS 9537 part-3 or surface mounted. | Mtrs | 10 | 240 | 2400 | [6 empty] | 2400
0
3 | Supply, installation, testing & commissioning of point wiring for Emargency light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included. | [10 empty] | 0
| Averagepoint length of primary&secondaryto be derived by Contractor, fromthe drawing provided AND+/-1MtrMeasured Radially | [10 empty] | 0
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | Nos. | 2 | 1750 | 3500 | 2 | 0 | 2 | 3500 | 0 | 3500 | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | Nos. | 9 | 1050 | 9450 | 9 | 0 | 9 | 9450 | 0 | 9450 | 0
0
5 | Providing point wiring for Raw Power/UPS points 1no. 6/16A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 4.0 sq. mm copper conductor wires and minimum 4.0 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect / Consultant. (Cost of GI Conduit / Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be LSZH type ) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially. | [10 empty] | 0
a) | Primary Point | Nos. | 8 | 2900 | 23200 | 8 | 0 | 8 | 23200 | 0 | 23200 | 0
b) | Secondary points | Nos. | 27 | 1600 | 43200 | 27 | 0 | 27 | 43200 | 0 | 43200 | 0
0
6 | Providing point wiring for Raw Power points 1no. 6A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 2.5 sq. mm copper conductor wires and minimum 2.5 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect / Consultant. (Cost of Conduit / Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be FRLS type ) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially. | [10 empty] | 0
a) | Primary Point | Nos. | RO | [8 empty] | 0
b) | Secondary points | Nos. | RO | [8 empty] | 0
0
0
8 | Supply and laying of following PVC insulated copper conductor 1100 volt grade stranded flexible LSZH wire in already laid GI conduit concealed or surface mounted making connections where ever required to complete the installation.(For Kitchen and Bar Power Points) Conduit rate shall be paid separately. | [10 empty] | 0
a) | 2R x 2.5Sqmm + 1R x 2.5Sqmm Cu. Wires | Mtr. | 60 | 225 | 13500 | 108 | 229 | 337 | 24300 | 51525 | 75825 | -62325
b) | 3R x 4Sqmm Cu. Wires | Mtr. | 240 | 310 | 74400 | 516 | 25 | 541 | 159960 | 7750 | 167710 | -93310
c) | 4R x 4Sqmm + 2R x 2.5Sqmm Cu. Wires | Mtr. | [9 empty] | 0
d) | 4R x 6Sqmm + 2R x 2.5Sqmm Cu. Wires | Mtr. | [9 empty] | 0
0
9 | Supply & installation of 25 mm dia. GI conduit with pull box / junction box & all accessories for Kitchen & Bar Power wiring as per the requirement | [10 empty] | 0
a | - do - but conduit pipe shall be Rigid type. | Mtr. | 350 | 185 | 64750 | 267 | 73 | 340 | 49395 | 13505 | 62900 | 1850
b | - do - but flexible conduit pipe | Mtr. | 25 | 85 | 2125 | 24 | 0 | 24 | 2040 | 0 | 2040 | 85
0
10 | Supply & installation of 20 mm dia. GI conduit with pull box / junction box & all accessories for Lighting & Power wiring as per the requirement | [10 empty] | 0
a | - do - but conduit pipe shall be Rigid type. | Mtr. | RO | [8 empty] | 0
b | - do - but flexible conduit pipe | Mtr. | RO | [8 empty] | 0
0
11 | Supply and installation of Perforated Cable Tray (ASIAN)out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant/Architect | [10 empty] | 0
a | 300 x 50 x 2mm | Mtr. | 30 | 900 | 27000 | [6 empty] | 27000
b | 200 x 50 x 2mm | Mtr. | RO | [8 empty] | 0
c | 150 x 50 x 2mm | Mtr. | 10 | 750 | 7500 | [6 empty] | 7500
d | 100 x 50 x 2mm | Mtr. | RO | [8 empty] | 0
e | 50 x 50 x 2mm | Mtr. | RO | [8 empty] | 0
0
12 | Supply and installation of GI trunking (SV POWER/ASIAN) with 2 mm thickness & properties/clamps for suspension at appropriate intervals & as per the route approved by Architect/Consultant. (For DATA/CONTROL WIRING/LIGHTING & POWER CIRCUITS / KITCHEN) | [10 empty] | 0
a | 300 x 50 x 2mm | Mtr. | RO | [8 empty] | 0
b | 200 x 50 x 2mm | Mtr. | RO | [8 empty] | 0
c | 150 x 50 x 2mm | Mtr. | 30 | 1000 | 30000 | 8 | 8 | 16 | 8000 | 8000 | 16000 | 14000
d | 100 x 50 x 2mm | Mtr. | RO | [8 empty] | 0
e | 50 x 50 x 2mm | Mtr. | RO | [8 empty] | 0
0
13 | Supply and installation of GI raceway with 2 mm thickness & proper ties/clamps at appropriate intervals & as per the route approved by Architect/Consultant. (Cost of cutting the floor for laying of raceways to be included). | [10 empty] | 0
a | 3 runs of underfloor raceways of size 100 x 40 mm | Mtr. | RO | [8 empty] | 0
b | 2 runs of underfloor raceways of size 100 x 40 mm | Mtr. | RO | [8 empty] | 0
c | 1 runs of underfloor raceways of size 100 x 40 mm | Mtr. | 20 | 650 | 13000 | [6 empty] | 13000
d | 1 runs of underfloor raceway of size 85 x 40 mm | Mtr. | RO | [8 empty] | 0
e | 2 runs of underfloor raceway of size 65 x 40 mm | Mtr. | RO | [8 empty] | 0
f | 1 runs of underfloor raceway of size 65 x 40 mm | Mtr. | 10 | 650 | 6500 | [6 empty] | 6500
0
14 | Supply & installation of GI junction boxes with 2 mm thickness, 2mm thick SS cover with 2” extra on all sides SS cover on top and having screw fixed plates on all four sides with knock out holes for conduits. The plates shall be retained on the sidezs having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be prepared as per the final approval of Architect/Consultant. The junction boxes shall be protected from the entry of unwanted material till the completion of the project & the SS plates shall be installed after the final polishing of flooring. | [10 empty] | 0
a | suitable for 450 x 450 x 50 mm | Nos. | RO | [8 empty] | 0
b | suitable for 350 x 350 x 50 mm | Nos. | RO | [8 empty] | 0
c | suitable for 250 x 250 x 50 mm | Nos. | 4 | 950 | 3800 | [6 empty] | 3800
d | suitable for 150 x 150 x 50 mm | Nos. | RO | [8 empty] | 0
0
15 | Supply, installation, testing & commissioning of flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect/Consultant | [10 empty] | 0
a | 6A one way plate type switch | Nos. | 2 | 185 | 370 | [6 empty] | 370
b | 6A 5 pin Socket outlet | Nos. | RO | [8 empty] | 0
c | 6A 5pin switch socket outlet for CCTV & Charging point | Nos. | 1 | 450 | 450 | [6 empty] | 450
f | 3 nos. 6A socket controlled by 1no 16A switch | Nos. | 2 | 730 | 1460 | [6 empty] | 1460
g | 2 nos. 6A socket controlled by 2no 16A switch | Nos. | [9 empty] | 0
| USB Point | Nos. | 5 | 750 | 3750 | 4 | 0 | 4 | 3000 | 0 | 3000 | 750
h | 1 nos. 6/16A socket controlled by1nos 6/16A switch | Nos. | 32 | 760 | 24320 | 22 | 22 | 44 | 16720 | 16720 | 33440 | -9120
0
l | I phase, 2 Nos x 5/15 amp, bakelite socket & switch, housed in Fabricated SS Panel suitable for hanging arrangement for Kitchen equipments. (having Two outlet /6 modular plate) | Nos. | 1 | 1300 | 1300 | [6 empty] | 1300
0
16 | Supplying, installation, Testing and commissioning flush mounting floor metallic boxes IP 66 (at terrace level) with 2 nos of 6/16A International switch & socket outlet + 1 set of blanking plate for 2 data/voice outlet suitable for AMP tyco I/o's of following modules complete with all installation kits, accessories, required to finish the installation – Sample will Approved by Client/Consultant. Cost of Switches, sockets outlet & blanking plat for Data/Voice outlets shall be included. | [10 empty] | 0
16.1 | 300mm x 300mm x 65/75 mm | Nos. | RO | [8 empty] | 0
0
17 | Supply, installation of temporary lighting & power arrangement for construction purpose of with industrial type switch & sockets/MCB's/ELCB's & lighting fittings as required to finish the work for interior contractor & necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules & regulations as per Airport Security Department. The material shall be taken back by the contractor. | Job | 1 | 12500 | 12500 | 1 | 0 | 1 | 12500 | 0 | 12500 | 0
0
| TOTAL FOR WIRING & ACCESSORIES | [10 empty] | 0
0
VI | LIGHTING FITTINGS | [10 empty] | 0
| Installation, testing & commissioning of the following concealed / surface mounted or suspended light fixtures AS PER FINAL APPROVAL FROM ARCHITECT/CLIENT/CONSULTANT with lamps, ballast & all necessary mounting & supporting accessories. No additional cost shall be paid for supporting. | [10 empty] | 0
0
1 | FILAMENT BULB | Nos. | 46 | 150 | 6900 | 31 | 0 | 31 | 4650 | 0 | 4650 | 2250
2 | PULLEY LIGHT | Nos. | 12 | 150 | 1800 | 11 | 0 | 11 | 1650 | 0 | 1650 | 150
3 | CHANDELIER | Nos. | 4 | 2000 | 8000 | 5 | 0 | 5 | 10000 | 0 | 10000 | -2000
4 | KEG LIGHT | Nos. | 3 | 250 | 750 | 3 | 0 | 3 | 750 | 0 | 750 | 0
5 | TRACK LIGHT | Nos. | 32 | 400 | 12800 | 28 | 0 | 28 | 11200 | 0 | 11200 | 1600
6 | DECORATIVE LIGHT | Nos. | 1 | 250 | 250 | 1 | 0 | 1 | 250 | 0 | 250 | 0
7 | HANGING SPOT LIGHT | Nos. | 12 | 250 | 3000 | 31 | 0 | 31 | 7750 | 0 | 7750 | -4750
8 | LED STRIP LIGHT | Mtr. | 47 | 400 | 18800 | 42 | 0 | 42 | 16800 | 0 | 16800 | 2000
9 | SPIKE LIGHT | Nos. | 12 | 250 | 3000 | 12 | 0 | 12 | 3000 | 0 | 3000 | 0
10 | FILAMENT LIGHT EMERGENCY | Nos. | 6 | 150 | 900 | [6 empty] | 900
11 | HANGING SPOT LIGHT EMERGENCY | Nos. | 5 | 250 | 1250 | [6 empty] | 1250
0
| TOTAL FOR LIGHTING FIXTURES | [10 empty] | 0
0
VII | EARTHING | [10 empty] | 0
1 | Supply and Installation of Maintenance Free Chemical earthing using Electrode of Size approx. 38 mm dia +/- 2mm, 3 metres long bonded with 50x6 copper internal strip complete with excavation, civil works, cast iron cover with backfill compound min. 40 KG. The system shall be CPRI tested. Warranty period of chemical earthing from the date of commissioning shall be 5 years. Warranty implies the voltage between earth and neutral will not exceed 0 volts for earthing pits installed. (Note: Body earthing provided by Base builder. We have considered Neutral earthing for UPS & Server racks.) | Nos. | RO | [8 empty] | 0
2 | Supply & erection of G.I. strip of 50 x 6 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | RO | [8 empty] | 0
3 | Supply & erection of G.I. strip of 25 x 3 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | 60 | 250 | 15000 | [6 empty] | 15000
4 | 1 no. 4 sq. mm YY cable in 25mm GI conduit for earthing FOR NETWORK RACK | Mtr. | 20 | 150 | 3000 | [6 empty] | 3000
5 | Supplying & erecting bare copper conductor of 8 swg for earthing purpose | Mtr. | 80 | 110 | 8800 | [6 empty] | 8800
7 | Supplying & erecting bare GI conductor of 8 swg for earthing purpose | Mtr. | [9 empty] | 0
8 | Supplying & erecting bare CU conductor of 12 swg for earthing purpose | Mtr. | [9 empty] | 0
9 | Supplying & installation testing & commissioning of earth terminal box | Nos. | [9 empty] | 0
0
| TOTAL FOR EARTHING | [10 empty] | 0
0
VIII | MISCELLANEOUS | [10 empty] | 0
1 | Supply & Installation of 6A 3 pin plug top | Nos. | RO | [8 empty] | 0
0
2 | Supply & Installation of 16A 3 pin plug top | Nos. | RO | [8 empty] | 0
0
3 | Supply, installation, testing & commissioning of Cat-6 FRLS Cable for Lighting Automation | Mtr. | RO | [8 empty] | 0
0
4 | Supply & laying of Rubber Mats, CPRI tested conforming to standards like BS 921, ASTM-D 178 & IEC 479 for different operatng voltage ratings as below. | [10 empty] | 0
| Supply of 2M x 1M Rubber mat suitable for operatng voltage upto 1.1 KV | Set | 1 | 3000 | 3000 | [6 empty] | 3000
0
5 | Supply & fixing of approved shock treatment chart written in English and in local Language. The chart shall be framed in Teakwood and covered with glass. | Nos. | 1 | 500 | 500 | [6 empty] | 500
0
6 | Supply & fixing of approved Fire Alarm evacuation plan chart written in English and in local Language approved by cleint requrements. | Nos | RO | [8 empty] | 0
0
7 | Supply & fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language | Nos. | 1 | 500 | 500 | [6 empty] | 500
0
8 | Supply & handed over to client of First Aid Box | Set | RO | [8 empty] | 0
0
9 | SITC of Emergency Exit signage (battery operated) approval by client / architect / consultant. Make: Prolite or Equivalent | Nos. | RO | [8 empty] | 0
0
| TOTAL FOR MISELANIOUS | [10 empty] | 0
0
IX | LOW VOLTAGE SYSTEM | [10 empty] | 0
0
A | DATA AND TELEPHONE SYSTEM | [10 empty] | 0
0
1 | Supply & Installation of 25mm.dia. GI conduit with pull box/ junction box & all accessories for DATA /VOICE/WIFI wiring as per the requirement. | Mtr. | 500 | 175 | 87500 | 147 | 67 | 214 | 25725 | 11725 | 37450 | 50050
0
2 | Providing DATA wiring inside 25mm dia GI conduit from each Data outlet to ICT CP Point by using Indoor Type CAT6A, | Mtr. | 450 | 90 | 40500 | 499 | 53 | 552 | 44910 | 4770 | 49680 | -9180
0
3 | Supply & Installation of Internet Jack Unit RJ-45 suitable for CAT6A | Nos. | 20 | 400 | 8000 | [6 empty] | 8000
0
4 | Supply & Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 3 Feet | Nos. | 20 | 400 | 8000 | [6 empty] | 8000
0
5 | Supply & Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 7 Feet | Nos. | 10 | 600 | 6000 | [6 empty] | 6000
0
6 | Supply & laying indoors multi-pair 0.5mm dia copper PVC insulated and sheathed, armoured telephone cables on walls, ceiling, cable trays, trunking complete with clamps, cable markers etc. from MDF to the various tag blocks as specified | [10 empty] | 0
a | 10 pair cable armoured | Mtr. | 40 | 280 | 11200 | [6 empty] | 11200
b | 5 pair cable | Mtr. | RO | [8 empty] | 0
c | 3 pair cable | Mtr. | RO | [8 empty] | 0
d. | 2 pair cable | Mtr. | RO | [8 empty] | 0
0
7 | Supply & installation of telephone tag block with KRONE terminal connectors, G.I.J.B as specified & com-plete with all interconnections and jumper connections bet-ween the two tag blocks on all floors as shown on drgs. | [10 empty] | 0
a | 50 pair tel. tag block | Nos. | RO | [8 empty] | 0
b | 20 pair tel. tag block | Nos. | 1 | 1500 | 1500 | [6 empty] | 1500
c | 10 pair tel. tag block | Nos. | RO | [8 empty] | 0
TOTAL FOR DATA AND TELEPHONE SYSTEM
| TOTAL |  |  |  | 1148285 |  |  |  | 851370 | 160295 | 1011665 | 136620
| GST 18% |  |  |  | 206691.3 |  |  |  | 153246.6 | 28853.1 | 182099.7 | 24591.6
| G. Total |  |  |  | 1354976.3 |  |  |  | 1004616.6 | 189148.1 | 1193764.7 | 161211.6

## PHE
The Irish House -LUCKNOW-PHE BOQ
Item No. | Description | Unit | Qty | Rate |  | Qty. |  |  | Amount in Rs. |  |  |  | Remarks
[5 empty] | Amount | Previous Bill | This Bill | Up To Date | Previous Bill | This Bill | Up To Date | Varation
A | WATER SUPPLY PIPING
1 | CPVC Pipes conforming to ASTM D-2846, SDR-11 grade and CPVC solvent weld fittings like elbows, tees, couplars, brass threaded adaptors, insert ring etc. suitable for (domestic and flushing) cold applications rated, concealed piping within wall / floor including jointing with fittings using solvent cement, brass threaded end fittings for making connection to fixtures. The work shall also include chasing the walls with machine wherever required for concealed piping and making good the same after laying of pipes & necessary pressure testing Chasing finishing shall be done with 1:1 cement mixed mortar, restore the same original condition for internal and shaft piping, including necessary hot deep galvanised supports vertical / horizontal, as per direction of Site incharge direction. [The rate shall include supply of S.S.screws and nut bolts etc.chasing in walls done by machine] (For Domestic and Flushing water-Toilet internal) (Pipe shall be tested with 1.5 times working pressure as covered in specifications)
1.1 | 20 mm Dia | R.mt | 35 | 550 | 19250 | 49.39 | 0 | 49.39 | 27164.5 | 0 | 27164.5 | -7914.5
1.2 | 25 mm Dia | R.mt | 0
1.3 | 32mm Dia | R.mt | 0
1.4 | 40mm Dia | R.mt | 0
2 | Providing & Fixing of gun metal heavy Ball Valves-PN-16 (approved makes as covered in specification) screwed type for water system of the following diameters. Valve shall have with unions.
2.1 | 20mm Dia | Nos. | 4 | 1850 | 7400 | 3 | 0 | 3 | 5550 | 0 | 5550 | 1850
2.2 | 25mm Dia | Nos. | 0
2.3 | 32mm Dia | Nos. | 0
2.4 | 40mm Dia | Nos. | 0
3 | Providing ,fixing, testing and commissioning capstan make Water Meter including providing & fixing matching Isolation valves ,strainer, non-return valve,complete with all necessary fittings etc screwed type(15Kgs/Sq.cm). Valve shall have with union.
3.1 | 20 mm Dia incoming line | Nos. | 1 | 2250 | 2250 | [6 empty] | 2250
3.2 | 25 mm Dia incoming line | Nos. | RO
3.3 | 32 mm Dia incoming line | Nos. | RO
4 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories
4.1 | 5 L Capacity- | Nos. | RO
4.2 | 20 L Capacity | Nos. | 1 | 28000 | 28000 | [6 empty] | 28000
4.3 | 35 L Capacity- For shower | Nos. | RO
5 | Supply, installation,testing & commissioning of Stiebel Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories (Optional in pantry)
5.1 | 3.5kw in pantry- optional | Nos. | RO
5.2 | 8kw | Nos. | RO
5.3 | 13kw-3ph- Subject to load permits | Nos. | RO
6 | SITC of Eco smart RO-50 with all required accessories .( Prior to order cpacaity and model to need to be confirmed by the kitchen consultant) | Nos | 1 | 21000 | 21000 | [6 empty] | 21000
7 | SITC of ACO grease trap -model Lipumobil 0.8 -Capacity -48 lit ( 0.8 LPS) with all required accessories ( Order shall be placed as per space available below the counter) | Nos | 0
8 | SITC of ACO grease trap -model Lipumobil S -Capacity -32 lit ( 0.5 LPS) with all required accessories | Nos | 0
B | DRAINAGE
1 | uPVC-SWR pipes conforming to IS 13592/92 including fittings conforming to IS-14935/99 and agri type pipes above 100 mm dia. conforming to IS: 4985, cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts / supported on wall / hung below slab etc. with all material & labor complete and as directed. [The Rate shall include supply and fixing of hotdip galvanised bracket nut bolts/ PVC Coated U-Clamp and screws] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] (For Soil , Waste, Vent and RWP-Internal and vertical shaft ).
1.1 | 40mm Dia | R.mt | 2 | 140 | 280 | [6 empty] | 280
1.2 | 50mm Dia | R.mt | 6 | 175 | 1050 | [6 empty] | 1050
1.3 | 65mm Dia | R.mt | 0
1.4 | 75mm Dia | R.mt | 7 | 210 | 1470 | 7.96 | 0 | 7.96 | 1671.6 | 0 | 1671.6 | -201.6
1.5 | 100 mm Dia | R.mt | 2 | 360 | 720 | [6 empty] | 720
1.6 | 150 mm Dia | R.mt | RO
2 | Supply, Install PVC Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 2 | 1350 | 2700 | 6 | 0 | 6 | 8100 | 0 | 8100 | -5400
3 | Supply, Install PVC Multi Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 4 | 1550 | 6200 | [6 empty] | 6200
4 | Supply, Install PVC urinal Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0
5 | Supply, Install PVC P- Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0
C | SANITARY AND C. P. FITTINGS & FIXTURES
Only installation, testing and commissioning of sanitary and C.P. fittings
1.1 | EWC with seat cover | Nos | 0
1.2 | Concealed flush tank | Nos | 0
1.3 | Concealed flush valve | Nos | 0
1.4 | Health Faucet | Nos | 0
1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 0
1.6 | Bided | Nos | R.O.
1.7 | Under Counter Wash Basin including waste Coupling | Nos | 0
1.8 | Wash Basin Cock | Nos | 0
1.9 | shower and mixer | Nos | 0
1.1 | Jet Spray | Nos | 0
1.11 | Bath Tub including waste Coupling and nessessary connections | Nos | 0
1.12 | Under Counter Sink including waste Coupling | Nos | 1 | 8600 | 8600 | [6 empty] | 8600
1.13 | Sink Pillar Cock | Nos | 1 | 1850 | 1850 | 1 | 0 | 1 | 1850 | 0 | 1850 | 0
1.14 | Bottle Trap for WHB/ sink and urinal with all connecting pipes | Nos | 1 | 2260 | 2260 | 1 | 0 | 1 | 2260 | 0 | 2260 | 0
1.15 | Angle Cock with PVC pipe connection upto WHB/sink/Geyser connection | Nos | 7 | 2200 | 15400 | 10 |  | 10 | 22000 | 0 | 22000 | -6600
1.16 | Urinal | Nos | 0
1.17 | Auto Flush Valve & Sensor with connecting piping & spreader for urinal(DC) | Nos | 0
D | S.S. GRATING
Only installations/ testing and commissioning of S.S.Gratings
1 | Making chamber in brick work including internal tiling etc for S.S Grating size, 1200mm x 200mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 0
2 | Making chamber in brick work including internal tiling etc for S.S Grating size, 600mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 1 | 12500 | 12500 | 1 | 0 | 1 | 12500 | 0 | 12500 | 0
4 | Making chamber in brick work including internal tiling etc for S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 3 | 7500 | 22500 | 3 | 0 | 3 | 22500 | 0 | 22500 | 0
| TOTAL A , B, C AND D |  |  |  | 153430 |  |  |  | 103596.1 | 0 | 103596.1 | 49833.9
| GST 18% |  |  |  | 27617.4 |  |  |  | 18647.298 | 0 | 18647.298 | 8970.102
| G.Total |  |  |  | 181047.4 |  |  |  | 122243.398 | 0 | 122243.398 | 58804.002

## HVAC
The Irish House -LUCKNOW-HVAC BOQ
Item No. | Description | Unit | Qty | Rate |  | Qty. |  |  | Amount in Rs. |  |  |  | Remarks
[5 empty] | Amount | Previous Bill | This Bill | Up To Date | Previous Bill | This Bill | Up To Date | Varation
Note: | Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) :
1.1 | CEILING SUSPENDED AHU :
Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications:
Frame Structure: It shall consist of 48mm Extruded Aluminium with thermal break profile.
Panel: 45mm +/- 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg/m3 or PUF insulation of 48 kg/m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI.
Filtration Section: It shall be provided with single stage washable type of prefilter 'MERV 8' first stage which shall be placed before coil section.
Coil Section: Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m/sec (500 fpm).
Drain Pan: Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation.
Fan Section: SISW / DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration.
Other Details : AHU to house control box/ terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over/ Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers / Fire Alarm Panel. Power cable from Terminal box to motor & control cabling of required size upto the thermostat / sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports & accessories required for installation.
Contractor shall design the chilled water coil according to the following conditions:
a. Coil air entering temperature - 75.4°F DB
b. Coil air leaving temperature - 54 deg. F DB/ 52.99 deg. F WB
c. Chilled water temperature entering - 6.0 deg. C/ 42.8 deg. F
d. Chilled water temperature leaving - 13.3 deg. C/ 55.9 deg. F
Make : VTS / Zeco / Citizen
Type Capacity Tonnage ESP No. of
(Cfm) TR (mm WG) Rows
a | CS AHU 2500 9.2 25 4/6
GENERAL NOTES:
a. | LHS & RHS VALVE station location to be confirmed.
b. | Fan outlet velocity - 1600 FPM
c. | Contractor shall submit static pressure calculation for all above units to Client/Consultant.
d. | Any change in motor HP shall be made at no extra cost to client.
e. | Fan efficiency shall be minimum 75%
f. | The cost shall be included liftting & shifting of each equipment / material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material / equipment.
SUB-TOTAL
2 | CHILLED WATER PIPING WITH INSULATION:
2.1 | CHW PIPE
SITC of MS Heavy duty class 'C' ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker/ paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. "Table E" of BS code for flange thickness to be adhered.
Make: Jindal Hissar / TATA
a | Φ 65 mm | Rmt | 110 | 1600 | 176000 | [6 empty] | 176000
| Φ 40 mm | Rmt | 30 | 1100 | 33000 | 13.12 | 0 | 13.12 | 14432 | 0 | 14432 | 18568
2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE
SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class "O" Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports.
Make: Armaflex & K-flex
a | Φ 65 mm | Rmt | 110 | 350 | 38500 | [6 empty] | 38500
| Φ 40 mm | Rmt | 30 | 300 | 9000 | 13.12 | 0 | 13.12 | 3936 | 0 | 3936 | 5064
2.3 | BALL VALVE
SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure: Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
Make: Zoloto / Audco / Kitz
a | Φ 40 mm | Nos. | 8 | 4950 | 39600 | 8 | 0 | 8 | 39600 | 0 | 39600 | 0
2.4 | BALL VALVE WITH Y-STRAINER
SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure: Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation.
Make: Zoloto / Audco / Kitz
a | Φ 40 mm | Nos. | 2 | 6250 | 12500 | 2 | 0 | 2 | 12500 | 0 | 12500 | 0
2.5 | PIBCV VALVES
SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with +/- 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal / POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
Make: Oventrop / Siemens / Danfoss
a | Φ 40 mm | Nos. | 2 | 6950 | 13900 | 2 | 0 | 2 | 13900 | 0 | 13900 | 0
2.6 | Auto Air Vent Valves
Make: Anergy / Flamco
Providing and fitting Auto Vent Valves.
a | SITC of Auto air vent in each risers & common headers & AHU. 3/4" auto vent valves at each coil / riser/ header. | Nos. | 4 | 2250 | 9000 | 4 | 0 | 4 | 9000 | 0 | 9000 | 0
2.7 | SITC of Pressure gauges & Thermometers
Make: H Guru / Waree
Necessary pressure gauges and thermometers 4" Dial type.
a | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg/CM2 | Nos. | 4 | 6000 | 24000 | 4 | 0 | 4 | 24000 | 0 | 24000 | 0
b | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9/12 inches, Thermometer, Range 0-50 deg C | Nos. | 4 | 1500 | 6000 | 4 | 0 | 4 | 6000 | 0 | 6000 | 0
c | Thermowells | Nos. | 8 | 1100 | 8800 | 8 | 0 | 8 | 8800 | 0 | 8800 | 0
d | SITC of Brass Test Plug of industrial grade mounting on water | Nos. | RO | 0
2.8 | INSULATED CONDENSATE DRAIN PIPE
SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees & reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
| Make: Supreme, Prince, Astral | [10 empty] | 0
a | Φ 25 mm | Rmt | 10 | 400 | 4000 | 10 | 0 | 10 | 4000 | 0 | 4000 | 0
b | Φ 32 mm | Rmt | 20 | 420 | 8400 | [6 empty] | 8400
NOTES FOR PIPING:
a | Cover all open pipe ends with muslin cloth during construction
b | Pipe cleaning & chemical treatment as per specs shall be included in the piping cost.
c | Unit rates for all indicated sizes of pipes & valves shall be furnished.
d | Cleaning/Painting of pipe before insulation shall be included in piping cost.
e | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant.
f | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
SUB-TOTAL
3 | SHEET METAL WORKS:
3.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
a | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | RO
b | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 10 | 1110 | 11100 | [6 empty] | 11100
c
d | FACTORY FABRICATED G.I FLAT OVAL DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Exposed Flat Oval ducting, Elbows with turning vanes, Splitters, Reducers, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. All exposed ducts has to be powder coated by HVAC contractor, sample and color code to be presented for the validation of Client / Architect.
3.2 | GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
| 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | RO
| 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 115 | 1350 | 155250 | 88.48 | 0 | 88.48 | 119448 | 0 | 119448 | 35802
3.3
EXTRUDED ALUMINIUM CEILING GRILLES
Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square/rectangular/Linear). The grilles shall be with 15/30/45° deflections as per requirement. The Colour shall be decided and approved by client and architect.
| Curve Grille | Sq.mtr | 1.5 | 6000 | 9000 | 1.08 | 0 | 1.08 | 6480 | 0 | 6480 | 2520
Make: Cosmos, Air Master & System Air
3.4
SPIGOT DAMPER FOR ELLIPTICAL DUCT
| Supply, installation and testing of galvanized steel construction dampers for circular ducts ( VCD ) within ducts provided with suitable lever and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | Sq.mtr | 0.5 | 5100 | 2550 | 0.5 | 0 | 0.5 | 2550 | 0 | 2550 | 0
Make: Cosmos, Air Master & System Air
3.5
OPPOSED BLADE DAMPER
| SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 1.5 | 6800 | 10200 | 1.08 | 0 | 1.08 | 7344 | 0 | 7344 | 2856
3.6
CANVAS CONNECTION
a | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
b | For AHU | Nos. | 2 | 3910 | 7820 | 2 | 0 | 2 | 7820 | 0 | 7820 | 0
3.7 | CURTAIN TYPE FIRE DAMPER
SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 / 225°F, etc; as per the approved shop drawings and specifications.
Make: Carryaire / System Air / Dynacraft / Air Master
a | Bare fire dampers | Sq.mtr | 0.5 | 9400 | 4700 | [6 empty] | 4700
b | Fusible link as per specification UL 555 | No | 1 | 2900 | 2900 | [6 empty] | 2900
NOTES:
The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
Muslin cloth cover for all air outlets during construction.
Pressure testing of complete duct work as per DW/ SMACNA standard.
Silicon sealant for longitudinal & transverse joints as per specification.
Diffusers & grilles shall be powder coated as per color approved by Architect.
SUB-TOTAL
4 | THERMAL & ACOUSTIC INSULATION:
4.1 | THERMAL INSULATION
| Supply & fixing of Thermal insulation for supply air duct using 13mm thick class " O " Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 100 | 675 | 67500 | 85.78 | 0 | 85.78 | 57901.5 | 0 | 57901.5 | 9598.5
Make: Armaflex & K-flex
4.2 | ACOUSTIC INSULATION
| Supply & fixing acoustic insulation for ducting using Class "1" closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal & transverse joints sealed with adhesive in neat & clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W/(m.K) and density of 140 - 180 kg/m³. | Sq.mtr | 25 | 865 | 21625 | 1.38 | 0 | 1.38 | 1193.7 | 0 | 1193.7 | 20431.3
Make: Armaflex & K-flex
Note:
a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
c. | Thermal insulation shall be internal for Elliptical / Expossed ducting.
SUB-TOTAL
5 | ELECTRICAL WORKS:
5.1 | STARTER PANEL
SITC of indoor / outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP & BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB/MCCB, Contactor, Bi-metal O/L relay with SPP, ON/OFF Push buttons, on / off / trip indication Lamp, on off push button, & phase indication Lamp. Selection of relay, contractor, MPCB/MCCB etc. as per Type-2 Coordination. Panel shall have provision to connect with BMS.
a | Suitable for 2500 CFM AHU, DOL Starter Panel | Nos. | 2 | 25350 | 50700 | 2 | 0 | 2 | 50700 | 0 | 50700 | 0
6.2 | POWER CABLING
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium /Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners/ Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
a | Suitable Power Cable:
| Suitable for 2500 CFM AHU, DOL Starter Panel | Rmt | 10 | 510 | 5100 | 41 | 0 | 41 | 20910 | 0 | 20910 | -15810
b | Earthing:
| 8 SWG | Rmt | 20 | 85 | 1700 | [6 empty] | 1700
6.3 | BTU METER
Supply,fixing and testing of inline Btu meter for the flow rate & temperature measurement consisting mainly of following 3 parts
a) Ultrasonic Flow Meter
b) Matched pair of temp sensor
c) Flowcell Sensor
c) BTU Meter - 4 - 20mA DC from flowmeter
Insertion type flowmeter shall be suitable for chilled water application for temp. Ranging from 0 to 50 deg C. Power supply shall be 240V AC (+/-) 15 %. Display shall have 16 characters LCD display with Back light, flow rate, Velocity, totaliser etc. Output shall be BMS Modbus compatible & shall have keypad lockout security option. It also should be able to show various units such as gallons, ft^3, lbs, liters, m^3, kg etc
Make: Honeywell / Danfoss / Siemens
a | Dia 65 mm | No. | 1 | 57000 | 57000 | [6 empty] | 57000
6.4 | CABLE TERMINATION :
Supply & Making of Cable termination of armoured / unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY & copper for 2XFY & YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing & commissioning of cables, meggaring values & submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools & dies shall be arranged by contractor.
a | Suitable for 2500 CFM AHU | Nos. | 4 | 1300 | 5200 | 4 | 0 | 4 | 5200 | 0 | 5200 | 0
6.5 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports.
a | 50mm wide | Rmt | 10 | 420 | 4200 | [6 empty] | 4200
SUB-TOTAL
| TOTAL |  |  |  | 799245 |  |  |  | 415715.2 | 0 | 415715.2 | 383529.8
| GST 18% |  |  |  | 143864.1 |  |  |  | 74828.736 | 0 | 74828.736 | 69035.364
| G. Total |  |  |  | 943109.1 |  |  |  | 490543.936 | 0 | 490543.936 | 452565.164
F

## Fire Fighting
The Irish House -LUCKNOW FIRE FIGHTING BOQ
Item No. | Description | Unit | Qty | Rate | Amount | Qty. |  |  | Amount in Rs. |  |  | Varation | Remarks
[6 empty] | Previous Bill | This Bill | Up To Date | Previous Bill | This Bill | Up To Date
1 | Providing, laying, jointing, testing and commissioning of G.I. `C' Class pipes (IS:1239 (Part-I)-1979) including cutting,threading welding etc providing all malleable galvanized iron fittings conforming to IS 1879, viz. Flanges, bends, tees, elbows,reducers, unions, supporting with G. I. clamps, hangers, M.S. brackets etc. including cutting holes and chases in brick or RCC wall / slabs and making good the same to the Approval of Architect / consultant,complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade. ( Note- Rigid pipe extension from existing line is considered)
i) | 25 mm dia. | RMT | 18 | 760 | 13680 | 30.145 | 0 | 30.145 | 22910.2 | 0 | 22910.2 | -9230.2
ii) | 32 mm dia. | RMT | 0
iii) | 40 mm dia. | RMT | 3 | 945 | 2835 | 13.31 | 0 | 13.31 | 12577.95 | 0 | 12577.95 | -9742.95
iv) | 50 mm dia. | RMT | 10 | 1050 | 10500 | 10.045 | 0 | 10.045 | 10547.25 | 0 | 10547.25 | -47.25
v) | 65 mm dia. | RMT | 5 | 1250 | 6250 | 11.35 | 0 | 11.35 | 14187.5 | 0 | 14187.5 | -7937.5
vi) | 80 mm dia. | RMT | 0
vii) | 100 mm dia. | RMT | 0
2 | Providing , fixing testing and commissioning of pendant type sprinkler heads 68 deg. Temp.(Quick response type) | No. | 0 | 650 | 0 | [6 empty] | 0
3 | Providing , fixing testing and commissioning of concealed type sprinkler heads 68 deg. Temp.(Extended coverage /Quick response type) | No. | 0
4 | Providing , fixing testing and commissioning of upright type sprinkler heads 68 deg. temp(Quick response type)- Optional Subject to liasion team requirements | No. | 0
5 | Providing , fixing testing and commissioning of upright type sprinkler heads 79 deg. Temp (Quick response type) | No. | 12 | 1350 | 16200 | 26 | 0 | 26 | 35100 | 0 | 35100 | -18900
6 | Providing & fixing testing and commissioning of braided UL Rated SS Flexible pipe
i) | 1 MT Long | No. | 0
ii) | 1.6 MT Long | No. | 12 | 4000 | 48000 | [6 empty] | 48000
7 | Gun metal chrome finished Ball valves (PN 16) with fittings of screwedend type.
I) | 40 mm dia. | No. | R.O.
I) | 32 mm dia. (Sprinkler drain-OPTIONAL) | Nos. | 1 | 1800 | 1800 | [6 empty] | 1800
8 | Butterfly Valves (PN 16) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification & to the level of satisfaction of Site- Incharge.
I) | 150 mm dia. | No. | R.O.
I) | 100 mm dia. | No. | R.O.
I) | 65 mm dia. (OPTIONAL) | No. | 2 | 6600 | 13200 | 2 | 0 | 2 | 13200 | 0 | 13200 | 0
9 | 6kg capacity ABC type dry chemical powder fire Extinguishers with wall mounting brackets | Nos. | 4 | 6500 | 26000 | 4 | 0 | 4 | 26000 | 0 | 26000 | 0
10 | 6kg capacity K type fire Extinguishers with wall mounting brackets | No. | 0
11 | 5kg capacity CO2 type fire Extinguishers with wall mounting brackets | No. | 2 | 8500 | 17000 | 2 | 0 | 2 | 17000 | 0 | 17000 | 0
12 | 9Lit AR-AFFF type fire Extinguishers with wall mounting brackets | Nos. | R.O.
13 | Flow switch on sprinkler distribution header on each floor with 2 SPDT contacts suitably rated, capable of the high pressure system and connected to fire alarm panel through cable.
i) | 100 mm dia. | No. | 0
14 | Ceasefire 5 Kg Ceiling Mounted Fire Extinguisher Clean Agent FE-36, Zero ODP, Stored Pressure Type, Pressure Gauge, Gross Weight 7.7 Kg, empty Weight 2.7 Kg, Can Height 264MM, Diameter 240MM,Discharge Time less than 8 Secs, Auto discharge mechanism on temperature rise, applicable on Class A,B,C and electrically started Fire, Can Construction : Deep drawn & Co2 Mig welded, Valve Construction : Forging & Machining, Internal Coating of Can : Epoxy Powder coating, External Coating of Can : Epoxy Polyster Powder coating, Sheet metal thickness : 2.0MM, Helium Leak Detection Test, 5 Years Warranty-model no 1CH21CF | No. | 0
| TOTAL |  |  |  | 155465 |  |  |  | 151522.9 | 0 | 151522.9 | 3942.1
| GST 18% |  |  |  | 27983.7 |  |  |  | 27274.122 | 0 | 27274.122 | 709.578
| G. Total |  |  |  | 183448.7 |  |  |  | 178797.022 | 0 | 178797.022 | 4651.678

## Fire Alarm
ADDRESSABLE FIRE ALARM BOQ FOR The {rish House @ LUCKNOW
SR.NO | DESCRIPTION | UNIT | TOTAL QTY. | Rates | Amount | Qty. |  |  | Amount in Rs. |  |  | Varation | Remarks
[6 empty] | Previous Bill | This Bill | Up To Date | Previous Bill | This Bill | Up To Date
A | ADDRESSABLE FIRE ALARM SYSTEM - NOTIFIER MAKE
1 | Analog Addressable Fire Alarm Control panel with battery back up for 24 hours normal operation and 15 minutes alarm operation. The control panel, battery charger etc. The panel shall be with 1 loop and expandable upto 2 loop capacity. The Fire Alarm Control Panel shall include a full featured operator interface control and annunciation panel that shall include a backlit 640-character liquid crystal display, individual, color coded system status LEDs, and a QWERTY style alphanumeric keypad for the field programming and control of the fire alarm system. Number of Loops / Fire alarm panels should be worked out based on loop capacity, It shall be selected keeping atlest 20 addresses as spare capacity in each loop. The control panel shall be capable of network expandable upto multiple panels. The panel & all devises should be FM approved and comply UL 864 or equivalent. The enclosure shall also be UL listed or equivalent The quoted rate shall include supply of necessary software and harware for progamming the panel with all necessary licence. Should have the Facility to get integrated with the MAIN FAS Panel of the Building. Electrical main LT panel, (PRO).Connecting to BMS on Bacnet or TCP/IP. | Nos | RO
i) Each loop with Min. 125 Devices & Detectors modules connection capability of Addressable FACP) 2 Loop Panel.
ii) FACP with all in-built modules & displays.
iii) 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working.
iv) Programming & setting up
v) system to be capable of operating the system for 2 hours during an emergency condition including all necessary software for remote programming of fire alarm system through central control station.
2 | Passive Repeater Panel with 80-Character (2x40) display with supervised power supply from FACP. Repeater Panel shall monitor and control (Scroll, Acknowledge, Reset & Mute) all the events of the FACP to which it is connected and it shall have Port Vectoring / Event Filtering capability of showing only ALARMS, TROUBLES or SUPERVISORY or customized combinations of user selected events. | Nos | RO.
2.1 | Supply installation and testing of signal loop components in a suitable galvanised steel junction box. | Nos. | 1
3 | Detectors and Devices
3.1 | Supply,Installation,Testing & Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices & shall be capable of providing DPDTcontact rated at 24V DC, 2A. | Nos | 2 | 5600 | 11200 | 2 | 0 | 2 | 11200 | 0 | 11200 | 0
3.2 | Supply,Installation,Testing & Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system and shall be capable of providing DPDTcontact rated at 24v DC, 2A. | Nos | 2 | 5600 | 11200 | 2 | 0 | 2 | 11200 | 0 | 11200 | 0
3.3 | Supply,Installation,Testing & Commissioning of wall / ceiling mounted Horn cum Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication and necessary accessories including back box. | Nos | 2 | 3700 | 7400 | 2 | 0 | 2 | 7400 | 0 | 7400 | 0
3.5 | Supply,Installation,Testing & Commissioning of above / below ceiling mounted Analogue Addressable Flash scan Type Photoelectric smoke detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 6 | 4300 | 25800 | 6 | 0 | 6 | 25800 | 0 | 25800 | 0
3.6 | Supply,Installation,Testing & Commissioning of above / below ceiling mounted Analogue Addressable Heat / Thermal detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 1 | 3700 | 3700 | 1 | 0 | 1 | 3700 | 0 | 3700 | 0
3.7 | Supply,Installation,Testing & Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressabla module that monitors and reports contact status. | Nos | 2 | 3300 | 6600 | 2 | 0 | 2 | 6600 | 0 | 6600 | 0
4 | Response indicator. | Nos | RO
NOTE: FIRE PANEL SHALL BE PROVIDED WITH FACILITY TO INTEGRATE WITH AIRPORT PANEL
5 | CABLES
Supplying, laying, testing and commissioning of 1100V grade FIRE RESISTANCE LOW SMOKE multicore, round type, insulated, sheathed, flexible copper conductor control cables with Including necessary end terminations with copper lugs, junction box, crimping identification tags at each end etc.,) RED COLOUR ONLY (MAKE: RR CABLE)
a | 2 core x 1.5 Sq.mm armoured cable(Un-screened, LSZH armoured) | Mtr | 220 | 120 | 26400 | 55 | 0 | 55 | 6600 | 0 | 6600 | 19800
6 | REWORKS
Shifting , relocation and reworking including extending of cable & testing and commissioning of the following devices
a | Photoelectric Smoke Detectors (BFC) at actuals. | Nos. | R.O.
b | Response Indicator of AFC detectors at actuals | Nos. | R.O.
| TOTAL FOR ADDRESSABLE FIRE ALARM SYSTEM |  |  |  | 92300 |  |  |  | 72500 | 0 | 72500 | 19800
| GST 18% |  |  |  | 16614 |  |  |  | 13050 | 0 | 13050 | 3564
| G.Total |  |  |  | 108914 |  |  |  | 85550 | 0 | 85550 | 23364

## CCTV
CCTV BOQ FOR The Irish House @ LUCKNOW
SR.NO | DESCRIPTION | UNIT | TOTAL QTY. | Total Rate | Amount | Qty. |  |  | Amount in Rs. |  |  | Varation | Remarks
[6 empty] | Previous Bill | This Bill | Up To Date | Previous Bill | This Bill | Up To Date
II | CCTV SURVIELLIANCE SYSTEM
1 | Supply, Istallation, Testing & Commissioning of 5MP HD Dome Camera Model No. DS-2CE76HOTITMFS | Nos. | 7 | 4300 | 30100 | 8 | 0 | 8 | 34400 | 0 | 34400 | -4300
2 | Supply & Installation of 230/12V -20A DC Power Supply Unit for Camera Make: MRE/ACOORD | Set | 1 | 20000 | 20000 | 1 | 0 | 1 | 20000 | 0 | 20000 | 0
3 | 4-Channel Embedded DVR, Real Time Recording @ CIF Resolution for all Channels or D1 Resolution on 1st Channel and rest at Real Time @ CIF , Support English OSD, 1 SATA slot available, 230VAC & TCP/IP Connectivity. (Honeywell Make, HDDVR1004 Model) | Nos |  | 0
4 | 8-Channel Embedded DVR, Real Time Recording @ CIF Resolution for all Channels or D1 Resolution on 1st Channel and rest at Real Time @ CIF , Support English OSD, 1 SATA slot available, 230VAC & TCP/IP Connectivity. (Honeywell Make, HDDVR1008 Model) | Nos | 1 | 5700 | 5700 | 1 | 0 | 1 | 5700 | 0 | 5700 | 0
5 | VGA Flat screen TFT 21" high resolution Monitor with power supply complete | No. | RO | 0
6 | 8 TB Hard Disk (15 Days) | No. | 1 | 14500 | 14500 | 1 | 0 | 1 | 14500 | 0 | 14500 | 0
| Supply & Instllation of Power connector | No. | 7 | 600 | 4200 | 8 | 0 | 8 | 4800 | 0 | 4800 | -600
| Supply & Installation of co-axial connector | No. | 14 | 600 | 8400 | 16 | 0 | 16 | 9600 | 0 | 9600 | -1200
7 | Supply & laying of 2C x 1.5 sq. mm non-FRLS flexible PVC insulated cable with GI conduit FOR POWER SUPPLY | Mtr | 245 | 85 | 20825 | [6 empty] | 20825
8 | Supply & laying of RT-3 Co-axial & Power FRLS Cable | Mtr | 245 | 160 | 39200 | 202 | 0 | 202 | 32320 | 0 | 32320 | 6880
9 | Supply & Laying of 25mm dia. GI Conduit | Mtr | 90 | 75 | 6750 | 45 | 0 | 45 | 3375 | 0 | 3375 | 3375
10 | Supply & laying of RG6 cable for video transmission from all cameras to DVR located in Server Room with PVC conduit. | Mtr | RO
| TOTAL FOR CCTV SYSTEM |  |  |  | 149675 |  |  |  | 124695 | 0 | 124695 | 24980
| GST 18% |  |  |  | 26941.5 |  |  |  | 22445.1 | 0 | 22445.1 | 4496.4
| G. Total |  |  |  | 176616.5 |  |  |  | 147140.1 | 0 | 147140.1 | 29476.4

## PA System
Thr Irish House @ LUCKNOW
PA SYSTEM BOQ
SR. No | DESCRIPTION | UNIT | TOTAL QTY. | Rate | Amount | Qty. |  |  | Amount in Rs. |  |  | Varation | Remarks
[6 empty] | Previous Bill | This Bill | Up To Date | Previous Bill | This Bill | Up To Date
A | PA/MUSIC SYSTEM EQUIPMENTS SUPPLY
1 | Supply & Installation of JBL make Loudspeaker (6 watt) CEILING SPKR to match with Airport PA System | Nos. | 8 | 13500 | 108000 | [6 empty] | 108000
2 | Supply of JBL make Loudspeaker 20 watt wall mount SPKR | Nos.
3 | Supply, installation, testing & commissioning of Control 24CT Microplus JBL make Speakers | Nos. | RO
4 | Supply of Amplifier with Line matching transformers | Nos. | RO
5 | Supply of DSP with Card Model No. BLU-100/BLU 102 | Nos. | RO
6 | Supply of ZONE CONTROLLER Model No. BLU-3 | Nos. | RO
7 | Supply of Paging Mic Model No. DST-995 | Nos. | RO
8 | Supply of DVD Player for BGM | Nos. | RO
9 | Supply & Laying of 2x2.5 Sq.mm FRLS Speaker Cable. The cost of conduit shall be paid separately. | Mtr. | 72 | 125 | 9000 | 64.1 | 0 | 64.1 | 8012.5 | 0 | 8012.5 | 987.5
10 | Supply of 3x1.5 Sq.mm FRLS Microphone Cable The cost of conduit shall be paid separately. | Mtr. | RO
11 | Supply of 12U (600mmx800mm) Equipment Rack | Nos. | 1 | 4300 | 4300 | [6 empty] | 4300
12 | Supply & Laying of 25mm dia. GI Conduit | Mtr. | 50 | 85 | 4250 | 47.6 | 0 | 47.6 | 4046 | 0 | 4046 | 204
| TOTAL FOR MUSIC SYSTEM EQUIPMENTS |  |  |  | 125550 |  |  |  | 12058.5 | 0 | 12058.5 | 113491.5
| GST 18% |  |  |  | 22599 |  |  |  | 2170.53 | 0 | 2170.53 | 20428.47
| G. Total |  |  |  | 148149 |  |  |  | 14229.03 | 0 | 14229.03 | 133919.97

## MB Electrical
MB -Electrical ,The Irish House RA-5th
SR. No | DESCRIPTION | UOM | Boq qty. | No. | Length | Width | Height | Total | Remarks
I | PANEL & SWITCHGEAR
1 | Supply, installation, testing & commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process and duly powder coated using Siemens Grey Shade No. RAL 7032. The frame structure, doors and gland plates shall have 2.0 mm thick sheets and partitions shall be with 1.6 mm thick CRCA sheet. Base channel size 75 x 40 x 6 mm of ISMC shall be provided. The panel shall be dust and vermin proof with neoprene gasket. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus bar shall be of tinned Copper with epoxy supports and shall be insulated with colour coded heat shrink sleeves. The control wiring min. 2,5 Sq.mm shall be ZHLS type. The Panel shall be provided with CTs, phase indication lamps, meters, relays and all switchgear, etc. as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant. All componants for Switchgears shall be L&T/Legrand
a | Providing & installing MAIN LT PANEL as per SLD & Spec.: | Set | 1
| Material supply at site |  |  | 1 | 1 |  |  | 1
| Total qty | Set | [5 empty] | 1
| Previous qty | Set | [5 empty] | 1
| This bill qty | set | [5 empty] | 0
63 Amps 4 pole, 16kA MCCB with Microprocessor Based overload, short circuit & Earth Fault protection, Energy manager (EM6400NG) with RS485 port for BMS connectivity & 4A with SP MCB with 100/5A-3 Nos., 15VA, CL-1 CT's for metering & of AE make and phase indicating lamps Vaishno make with SPMCB. CBCT with microprocesor based EFR
Busbar chamber - 1 set, 4 pole 100A Tinned Cu. Busbar with necessary
OUTGOINGS:
i. | 63A 4P MCB – 1 Nos.
ii. | 40A 4P MCB – 2 Nos.
iii. | 40A DP MCB – 2 Nos.
iv. | MPCB suitable for 2.2kW-2 Nos.
2 | Supply, installation, testing & commissioning of Switchgears.(Standard Product)
a | Supply,Installation,Testing and Commissioning of 40 Amps,4Pole MCB with ELCB at 300mAh for HVAC Outdoor Isolation all complete with mounting accessories | Nos. | RO
b | Supply,Installation,Testing and Commissioning of 32 Amps,4Pole MCB for HVAC Outdoor Isolation all complete with mounting accessories. | Nos. | 2
c | Supply,Installation,Testing and Commissioning of 40 Amps, DP, MCB for UPS/INVERTER Isolation all complete with mounting accessories for UPS. | Nos. | 2
| UPS isolation DB and MCB set |  |  | 2 |  |  |  | 2
| Total Qty | Nos. | [5 empty] | 2
| Previous Qty | Nos. | [5 empty] | 2
| This Bill Qty | Nos. | [5 empty] | 0
d | Supply & installation of DOL starter L&T/Siemens/Legrand for 3 kW load | Nos. | RO
e | Supply & installation of DOL starter L&T/Siemens/Legrand for 4 kW load | Nos. | RO
f | Supply & installation of Star Delta starter as per Type-2 Coordination for 3 kW (4HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Exhaust air fan)(EXISTING UNIT PROVIDED BY MALL) | Nos. | RO
g | Supply & installation of Star Delta starter as per Type-2 Coordination for 9.3 kW (12.5HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Exhaust air fan) | Nos. | RO
h | Supply & installation of Star delta starter as per Type-2 Coordination for 5.5 kW (7.5HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Fresh air fan) | Nos. | RO
i | Supply & installation of DOL starter as per Type-2 Coordination for 2.2 kW (3.0HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For AHU) | Nos. | RO
j | Supply & installation of DOL starter as per Type-2 Coordination for 1.5 kW (2.0HP) pump load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Scrubber) | Nos. | RO
k | 80 amps 4P ELMCB 300mA with 63A 5 Pin Ray Roll Socket complete with all mounting accessories – for Indoor Legrand make model No. 6078 80 | Nos. | RO
l | 63 amps 4P ELMCB 300mA with 63A 5 Pin Ray Roll Socket complete with all mounting accessories – for Indoor Legrand make model No. 6078 80 | Nos. | RO
m | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make model No. 6078 80 | Nos. | RO
n | 25 amps 4P MCB with 25A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make model No. 6078 80 | Nos. | RO
o | 25A Rey roll socket complete with 25 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | Nos. | RO
p | 20A Rey roll socket complete with 32 amps DPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | Nos. | 1
q | 5/15A Rey roll socket complete with 15 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | Nos. | 7
r | Set of 1no 25A Metal clad Socket with MCB, and 2nos 6/16A Switch sockets housed in Fabricated SS Panel suitable for hanging arrangement for Kitchen equipments. | Nos. | RO
q | 5/15A Swicth socket complete (IP-65) for Kitchen | Nos. | 20
| Swicth socket ip65 for kitchen | Nos. |  | 10 |  |  |  | 10
| Total Qty | Nos | [5 empty] | 10
| Previous qty | Nos | [5 empty] | 10
| This bill qty | nos | [5 empty] | 0
3 | SITC of Standalone Gas leak detector with inbuilt sounder for Kitchen | Nos. | RO
TOTAL FOR MAIN PANEL & SWITCHGEAR
II | INVERTER / UPS
1 | Supply, Installation, testing and commissioning of 6 KVA UPS System Single Phase I/C & Single Phase O/G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings & the specifications. | Nos | 1
| UPS | Nos. |  | 1 |  |  |  | 1
| Total Qty | Nos | [5 empty] | 1
| Previous qty | Nos | [5 empty] | 1
| This bill qty | nos | [5 empty] | 0
TOTAL FOR UPS
III' | DISTRIBUTION BOARDS
Supply, installation, testing & commissioning of Distribution Boards surface / flush mounted with Double door containing MCB/ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs/RCCB should be of 30mA/100 mA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be 'D' type and other MCBs shall be 'C' category for lighting and raw power DB LEGRAND/L&T
1 | Lighting Distribution Board - LPDB | Nos. | 1
12 WAY TPN DB
I/C- 1 # 40A FP MCB , 16KA
SUB I/C - 3 # 25A DP RCCB 30mA per phase
O/G - 30 # 10/20A SP MCB
| Distribution board | Nos. |  | 1 |  |  |  | 1
| Total Qty | Nos. | [5 empty] | 1
| Previous bill | Nos. | [5 empty] | 1
| this bill qty | Nos. | [5 empty] | 0
2 | RAW Power Distribution Board - RPDB | Nos. | RO
6(8) WAY TPN DB
I/C- 1 #40 A FP MCB
SUB I/C- 3#40 DP ELCB 300mA per ph
O/G - 18 # 16/20A SP MCB
3 | Kitchen Power DB - (KPDB-1) | Nos. | 2
8 WAY TPN DB
I/C- 1 #40 A FP MCB
SUB I/C- 3#32 DP ELCB 100mA per ph
O/G - 18 # 16/20A SP MCB
| Supply kitchen dB | Nos. |  | 1 |  |  |  | 1
| Total Qty | Nos. | [5 empty] | 1
| Previous bill | Nos. | [5 empty] | 1
| this bill qty | Nos. | [5 empty] | 0
4 | EMERGENCY LIGHTING DB (ELDB/UPSDB) | Nos. | 1
12 way SPN DB
Incomer: 40A DP RCBO 30mA
Outgoings :10/16 SP MCB, 'D' Type – 8 Nos
| Emergency DB | Nos. |  | 1 |  |  |  | 1
| Total Qty | Nos. | [5 empty] | 1
| Previous bill | Nos. | [5 empty] | 1
| this bill qty | Nos. | [5 empty] | 0
TOTAL FOR DISTRIBUTION BOARDS
IV | CABLES & ACCESSORIES
Supply & installation of following LT XLPE FRLSH cables (FINOLEX/RR KABLE/POLYCAB) rated for 600 / 1100 volts AC as per IS standard 1554 Part 1 with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20 mtrs and ten finally with metal identification tags showing the size and the location from/to the specific Panel/DB at both ends.
1 | 3.5C x 300 Sq. mm A2XFY | Mtr. | RO
2 | 3.5C x 240 Sq. mm A2XFY | Mtr. | RO
3 | 3.5C x 185 Sq. mm A2XFY | Mtr. | RO
4 | 3.5C x 150 Sq. mm A2XFY | Mtr. | RO
5 | 3.5C x 120 Sq. mm A2XFY | Mtr. | RO
6 | 3.5C x 95 Sq. mm A2XFY | Mtr. | RO
7 | 3.5C x 70 Sq. mm A2XFY | Mtr. | RO
8 | 3.5C x 50 Sq. mm A2XFY | Mtr. | RO
9 | 3.5C x 35 Sq. mm A2XFY | Mtr. | RO
10 | 4C x 16 Sq. mm A2XFY | Mtr. | 100
11 | 4C x 10 Sq. mm A2XFY | Mtr. | RO
12 | 4C x 10 Sq. mm 2XFY ( Cu ) | Mtr. | RO
13 | 4C x 16 Sq. mm 2XFY ( Cu ) | Mtr. | RO
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 30
| main pannel to light DB | Mtr. |  | 1 | 3 |  |  | 3
| Main Pannel to Kitchen DB | Mtr. |  | 1 | 5 |  |  | 5
| Total Qty | mtr | [5 empty] | 8
| Previous bill | mtr | [5 empty] | 3
| this bill qty | mtr | [5 empty] | 5
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 60
16 | 4C x 2.5 Sq. mm 2XFY Cable ( Cu ) | Mtr. | RO
17 | 3C x 6sq. mm YWY cable ( Cu ) | Mtr. | 20
| UPS to Main Pannel | Mtr. |  | 1 | 16 |  |  | 16
| Total Qty | mtr | [5 empty] | 16
| Previous bill | mtr
| this bill qty | mtr | [5 empty] | 16
18 | 3C x 4sq. mm YWY cable ( Cu ) | Mtr. | 40
| AHU Stater to Main Pannel | Mtr. |  | 1 | 8 |  |  | 8
| Total Qty | mtr | [5 empty] | 8
| Previous bill | mtr
| this bill qty | mtr | [5 empty] | 8
19 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | Mtr. | RO
20 | 1C x 10 Sq. mm YY cable ( Cu ) | Mtr. | RO
21 | 1C x 6 Sq. mm YY cable ( Cu ) | Mtr. | RO
22 | 1C x 4 Sq. mm YY cable ( Cu ) | Mtr. | RO
23 | 5Rx1Cx16 Sq.mm YY FRLS Cable (Cu) | Mtr. | RO
24 | 5Rx1Cx10 Sq.mm YY FRLS Cable (Cu) | Mtr. | RO
25 | 5Rx1Cx6 Sq.mm YY FRLS Cable (Cu) | Mtr. | RO
26 | 5Rx1Cx4 Sq.mm YY FRLS Cable (Cu) | Mtr. | RO
B | Termination of following sizes of cables with Single compression cable gland.(COMET/BRAKO)
1 | 3.5C x 300 Sq. mm A2XFY | Nos. | RO
2 | 3.5C x 240 Sq. mm A2XFY | Nos. | RO
3 | 3.5C x 185 Sq. mm A2XFY | Nos. | RO
4 | 3.5C x 150 Sq. mm A2XFY | Nos. | RO
5 | 3.5C x 120 Sq. mm A2XFY | Nos. | RO
6 | 3.5C x 95 Sq. mm A2XFY | Nos. | RO
7 | 3.5C x 70 Sq. mm A2XFY | Nos. | RO
8 | 3.5C x 50 Sq. mm A2XFY | Nos. | RO
9 | 3.5C x 35 Sq. mm A2XFY | Nos. | RO
10 | 4C x 16 Sq. mm A2XFY | Nos. | 2
| Cable gland | Nos. |  | 1 | 1 |  |  | 1
| Total Qty | mtr | [5 empty] | 1
| Previous bill | mtr
| this bill qty | mtr | [5 empty] | 1
11 | 4C x 10 Sq. mm A2XFY | Nos. | RO
12 | 4C x 10 Sq. mm 2XFY ( Cu ) | Nos. | RO
13 | 4C x 16 Sq. mm 2XFY ( Cu ) | Nos. | RO
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | Nos. | 6
| Cable gland | Nos. |  | 1 | 3 |  |  | 3
| Total Qty | mtr | [5 empty] | 3
| Previous bill | mtr
| this bill qty | mtr | [5 empty] | 3
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) | Nos. | 4
16 | 4C x 2.5 Sq. mm 2XFY Cable ( Cu ) | Nos. | RO
17 | 3C x 6sq. mm YWY cable ( Cu ) | Nos. | 4
18 | 3C x 4sq. mm YWY cable ( Cu ) | Nos. | 4
19 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | Nos. | RO
20 | 1C x 10 Sq. mm YY cable ( Cu ) | Nos. | RO
21 | 1C x 6 Sq. mm YY cable ( Cu ) | Nos. | RO
22 | 1C x 4 Sq. mm YY cable ( Cu ) | Nos. | RO
23 | 5Rx1Cx16 Sq.mm YY FRLS Cable (Cu) | Nos. | RO
24 | 5Rx1Cx10 Sq.mm YY FRLS Cable (Cu) | Nos. | RO
25 | 5Rx1Cx6 Sq.mm YY FRLS Cable (Cu) | Nos. | RO
26 | 5Rx1Cx4 Sq.mm YY FRLS Cable (Cu) | Nos. | RO
TOTAL FOR CABLES & ACCESSORIES
V | WIRING & ACCESSORIES
Notes :
1) Rates for point wiring shall include supply & installation of Wires & wiring acccessories such as angle holders/ceiling roses as required. conduits, conduit accessories such as junction boxes, Ts, elbows etc,Switches, sockets & fixtures shall not be included in the point wiring rates. These will be counted & paid separately.
2) Unless otherwise specified, all wires in point wiring shall be 2.5 sq.mm
Stranded copper conductor 1.1 KV grade, I.S.I. marked (P+N+E),
LSZH) PVC insulated .
Wires shall be colour coded (Red, Yellow and Blue for Phases,
Black for Neutral & Green for earth).
3) Looping of wires shall be in fittings and switch boxes only
4) Location of switches/sockets/ DBs shown on the drawings shall
be confirmed with the Architect/ Consultant/ Project Manager
before installation.
5) All Surface and concealed Conduits shall be rigid GI conduits of
size not less than 20 mm dia as per applicable IS.
6)The Contractor can take more than one circuit in the same conduit
provided they are of the same phase. The size of conduit shall be
decided according to the number of wires in it as per applicable IS & as
specified.
7) Payments for light fixtures & fans will be made separately as per the
items given in 'Light Fixtures & Accessories'.
8) Type & location of light fixtures shown in the drawings are
tentative and subject to revision as per the recommendation of
Architect/ Consultant. The quantities (number of points and accessories)
of point wiring will be revised as actual installed on account of such
revisions in the layouts.
9) Circuit wiring from DBs to the switch boards or first light point shall
Be included as primary points & remaining points of the same looping
shall be considered as Secondary points and shall be counted in nos.
10) Circuit Wiring from DB to Kitchen Power points shall be measured in running meters
1 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included.
Averagepoint length of primary&secondaryto be derived by Contractor, fromthe drawing provided AND+/-1MtrMeasured Radially
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | Nos. | 20
| Light points |  |  | 21 |  |  |  | 21
| Total Qty | Nos. | [5 empty] | 21
| Previous bill | Nos. | [5 empty] | 21
| this bill qty | Nos. | [5 empty] | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | Nos. | 90
| secondary light point | Nos. |  | 98 |  |  |  | 98
|  | Nos. |  | 32 |  |  |  | 32
| Total Qty | Nos. | [5 empty] | 130
| Previous bill | Nos. | [5 empty] | 98
| this bill qty | Nos. | [5 empty] | 32
2 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Switch Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same switch board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI. conduits, 6A switch & switch board and accessories shall be included.
a) | Primary Light points controlled by Switch (3R x 2.5 sqmm wire) | Nos. | 1
| Light points |  |  | 1 |  |  |  | 1
| Total Qty | Nos. | [5 empty] | 1
| Previous bill | Nos. | [5 empty] | 1
| this bill qty | Nos. | [5 empty] | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | Nos. | 2
| Secondary Light |  |  | 2 |  |  |  | 2
| Total Qty | Nos. | [5 empty] | 2
| Previous bill | Nos. | [5 empty] | 2
| this bill qty | Nos. | [5 empty] | 0
c) | DB to SB & SB to SB circuit wiring : For Switch Operated Primary point @ SB to SB loop point. Wiring for switch board controlled by MCB already installed in DB by using 3 X 2.5 sq. mm flexible LSZH copper wires in 25mm GI conduits as per IS 9537 part-3 or surface mounted. | Mtrs | 10
3 | Supply, installation, testing & commissioning of point wiring for Emargency light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included.
Averagepoint length of primary&secondaryto be derived by Contractor, fromthe drawing provided AND+/-1MtrMeasured Radially
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | Nos. | 2
| Primary light point |  |  | 2 |  |  |  | 2
| Total Qty | Nos. | [5 empty] | 2
| Previous bill | Nos. | [5 empty] | 2
| this bill qty | Nos. | [5 empty] | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | Nos. | 9
| secondary light point |  |  | 9 |  |  |  | 9
| Total Qty | Nos. | [5 empty] | 9
| Previous bill | Nos. | [5 empty] | 9
| this bill qty | Nos. | [5 empty] | 0
5 | Providing point wiring for Raw Power/UPS points 1no. 6/16A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 4.0 sq. mm copper conductor wires and minimum 4.0 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect / Consultant. (Cost of GI Conduit / Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be LSZH type ) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | Nos. | 8
| Primary light point |  |  | 8 |  |  |  | 8
| TV POINT Addetional item |  |  | 2
| Total Qty | Nos. | [5 empty] | 8
| Previous bill | Nos. | [5 empty] | 8
| this bill qty | Nos. | [5 empty] | 0
b) | Secondary points | Nos. | 27
| secondary light point |  |  | 27 |  |  |  | 27
| Total Qty | Nos. | [5 empty] | 27
| Previous bill | Nos. | [5 empty] | 27
| this bill qty | Nos. | [5 empty] | 0
6 | Providing point wiring for Raw Power points 1no. 6A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 2.5 sq. mm copper conductor wires and minimum 2.5 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect / Consultant. (Cost of Conduit / Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be FRLS type ) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | Nos. | RO
b) | Secondary points | Nos. | RO
8 | Supply and laying of following PVC insulated copper conductor 1100 volt grade stranded flexible LSZH wire in already laid GI conduit concealed or surface mounted making connections where ever required to complete the installation.(For Kitchen and Bar Power Points) Conduit rate shall be paid separately.
a) | 2R x 2.5Sqmm + 1R x 2.5Sqmm Cu. Wires | Mtr. | 60
Lighting
| Y6 | Rmt. |  | 1 | 27 |  |  | 27
| R3 | Rmt. |  | 1 | 11 |  |  | 11
| B2 | Rmt. |  | 1 | 15 |  |  | 15
| B4 | Rmt. |  | 1 | 16 |  |  | 16
| B3 | Rmt. |  | 1 | 14 |  |  | 14
UPS kitchen
| F3 | Rmt. |  | 1 | 25 |  |  | 25
| RO | Rmt. |  | 1 | 25 |  |  | 25
| UPS F2 spike light in Rafters | Rmt. |  | 1 | 42 |  |  | 42
| UPS F1 spike light in Rafters | Rmt. |  | 1 | 49 |  |  | 49
| Sinage -1 | Rmt. |  | 1 | 18 |  |  | 18
| Sinage -2 | Rmt. |  | 1 | 21 |  |  | 21
| Projector | Rmt. |  | 1 | 21 |  |  | 21
| TV-1 F5 | Rmt. |  | 1 | 25 |  |  | 25
| TV-2 F6 | Rmt. |  | 1 | 28 |  |  | 28
| Total Qty. | Rmt | [5 empty] | 337
| Previous qty | Rmt | [5 empty] | 108
| This qty. | Rmt | [5 empty] | 229
b) | 3R x 4Sqmm Cu. Wires | Mtr. | 240
kitchen circuit KP DB
| R1 | Rmt. |  | 1 | 25 |  |  | 25
| R3 | Rmt. |  | 1 | 24 |  |  | 24
| Y1 | Rmt. |  | 1 | 23.5 |  |  | 23.5
| B3 | Rmt. |  | 1 | 22.5 |  |  | 22.5
| Y5 | Rmt. |  | 1 | 22 |  |  | 22
| Y4 | Rmt. |  | 1 | 22.5 |  |  | 22.5
| Y2 | Rmt. |  | 1 | 24 |  |  | 24
| B1 | Rmt. |  | 1 | 25 |  |  | 25
| R2 | Rmt. |  | 1 | 24.5 |  |  | 24.5
| B2 | Rmt. |  | 1 | 25 |  |  | 25
| Y3 | Rmt. |  | 1 | 25 |  |  | 25
| B4 | Rmt. |  | 1 | 25 |  |  | 25
Power point LP DB
| Y9 | Rmt. |  | 1 | 38 |  |  | 38
| Y8 | Rmt. |  | 1 | 18 |  |  | 18
| R8 | Rmt. |  | 1 | 36 |  |  | 36
| B7 | Rmt. |  | 1 | 35 |  |  | 35
| B8 | Rmt. |  | 1 | 25 |  |  | 25
| R9 | Rmt. |  | 1 | 22 |  |  | 22
Service UPS DB
| F4 | Rmt. |  | 1 | 19 |  |  | 19
| F5 | Rmt. |  | 1 | 35 |  |  | 35
| R Gyser | Rmt. |  | 1 | 25 |  |  | 25
| Total Qty | Rmt | [5 empty] | 541
| Previous Qty | Rmt | [5 empty] | 516
| this Bill Qty | Rmt | [5 empty] | 25
c) | 4R x 4Sqmm + 2R x 2.5Sqmm Cu. Wires | Mtr.
d) | 4R x 6Sqmm + 2R x 2.5Sqmm Cu. Wires | Mtr.
9 | Supply & installation of 25 mm dia. GI conduit with pull box / junction box & all accessories for Kitchen & Bar Power wiring as per the requirement
a | - do - but conduit pipe shall be Rigid type. | Mtr. | 350
|  | Rmt |  | 1 | 36 |  |  | 36
|  | Rmt |  | 1 | 16 |  |  | 16
|  | Rmt |  | 1 | 19 |  |  | 19
|  | Rmt |  | 1 | 19 |  |  | 19
|  | Rmt |  | 1 | 19 |  |  | 19
|  | Rmt |  | 1 | 19 |  |  | 19
|  | Rmt |  | 1 | 19 |  |  | 19
|  | Rmt |  | 1 | 19 |  |  | 19
|  | Rmt |  | 1 | 19 |  |  | 19
|  | Rmt |  | 1 | 8 |  |  | 8
| Cat 6 Wiring for TV-01 | Rmt |  | 1 | 24 |  |  | 24
| Cat 6 Wiring for TV-02 | Rmt |  | 1 | 24 |  |  | 24
|  | Rmt |  | 1 | 26 |  |  | 26
| Ceiling conduit | Rmt |  | 1 | 26 |  |  | 26
|  | Rmt |  | 1 | 10 |  |  | 10
|  | Rmt |  | 1
|  | Rmt |  | 1 | 26 |  |  | 26
|  | Rmt |  | 1 | 11 |  |  | 11
| Total Qty | Rmt | [5 empty] | 340
| Previous Qty | Rmt | [5 empty] | 267
| this Bill Qty | Rmt | [5 empty] | 73
b | - do - but flexible conduit pipe | Mtr. | 25
|  | Rmt |  | 1 | 3 |  |  | 3
|  | Rmt |  | 1 | 2 |  |  | 2
|  | Rmt |  | 1 | 2 |  |  | 2
|  | Rmt |  | 1 | 2 |  |  | 2
|  | Rmt |  | 1 | 2 |  |  | 2
|  | Rmt |  | 1 | 3 |  |  | 3
|  | Rmt |  | 1 | 3 |  |  | 3
|  | Rmt |  | 1 | 4 |  |  | 4
|  | Rmt |  | 1 | 3 |  |  | 3
| Total Qty | Rmt | [5 empty] | 24
| Previous Qty | Rmt | [5 empty] | 24
| this Bill Qty | Rmt | [5 empty] | 0
10 | Supply & installation of 20 mm dia. GI conduit with pull box / junction box & all accessories for Lighting & Power wiring as per the requirement
a | - do - but conduit pipe shall be Rigid type. | Mtr. | RO
b | - do - but flexible conduit pipe | Mtr. | RO
11 | Supply and installation of Perforated Cable Tray (ASIAN)out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant/Architect
a | 300 x 50 x 2mm | Mtr. | 30
b | 200 x 50 x 2mm | Mtr. | RO
c | 150 x 50 x 2mm | Mtr. | 10
d | 100 x 50 x 2mm | Mtr. | RO
e | 50 x 50 x 2mm | Mtr. | RO
12 | Supply and installation of GI trunking (SV POWER/ASIAN) with 2 mm thickness & properties/clamps for suspension at appropriate intervals & as per the route approved by Architect/Consultant. (For DATA/CONTROL WIRING/LIGHTING & POWER CIRCUITS / KITCHEN)
a | 300 x 50 x 2mm | Mtr. | RO
b | 200 x 50 x 2mm | Mtr. | RO
c | 150 x 50 x 2mm | Mtr. | 30
| DB Pannel Back Wall | Mtr. |  | 8 |  |  |  | 8
| DB Pannel Back Wall | Mtr. |  | 2 |  |  |  | 2
| Kitchen area | Mtr. |  | 6 |  |  |  | 6
| Total Qty | Rmt | [5 empty] | 16
| Previous Qty | Rmt | [5 empty] | 8
| this Bill Qty | Rmt | [5 empty] | 8
d | 100 x 50 x 2mm | Mtr. | RO
e | 50 x 50 x 2mm | Mtr. | RO
13 | Supply and installation of GI raceway with 2 mm thickness & proper ties/clamps at appropriate intervals & as per the route approved by Architect/Consultant. (Cost of cutting the floor for laying of raceways to be included).
a | 3 runs of underfloor raceways of size 100 x 40 mm | Mtr. | RO
b | 2 runs of underfloor raceways of size 100 x 40 mm | Mtr. | RO
c | 1 runs of underfloor raceways of size 100 x 40 mm | Mtr. | 20
d | 1 runs of underfloor raceway of size 85 x 40 mm | Mtr. | RO
e | 2 runs of underfloor raceway of size 65 x 40 mm | Mtr. | RO
f | 1 runs of underfloor raceway of size 65 x 40 mm | Mtr. | 10
14 | Supply & installation of GI junction boxes with 2 mm thickness, 2mm thick SS cover with 2” extra on all sides SS cover on top and having screw fixed plates on all four sides with knock out holes for conduits. The plates shall be retained on the sidezs having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be prepared as per the final approval of Architect/Consultant. The junction boxes shall be protected from the entry of unwanted material till the completion of the project & the SS plates shall be installed after the final polishing of flooring.
a | suitable for 450 x 450 x 50 mm | Nos. | RO
b | suitable for 350 x 350 x 50 mm | Nos. | RO
c | suitable for 250 x 250 x 50 mm | Nos. | 4
d | suitable for 150 x 150 x 50 mm | Nos. | RO
15 | Supply, installation, testing & commissioning of flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect/Consultant
a | 6A one way plate type switch | Nos. | 2
b | 6A 5 pin Socket outlet | Nos. | RO
c | 6A 5pin switch socket outlet for CCTV & Charging point | Nos. | 1
f | 3 nos. 6A socket controlled by 1no 16A switch | Nos. | 2
g | 2 nos. 6A socket controlled by 2no 16A switch | Nos.
| USB Point | Nos. | 5
|  | Nos. |  | 4 |  |  |  | 4
| Total Qty | Nos. | [5 empty] | 4
| Previous Qty | Nos. | [5 empty] | 4
| this Bill Qty | Nos. | [5 empty] | 0
h | 1 nos. 6/16A socket controlled by1nos 6/16A switch | Nos. | 32
|  | Nos. |  | 20 |  |  |  | 20
| tv switch socket | Nos. |  | 2 |  |  |  | 2
|  | Nos. |  | 18 |  |  |  | 18
| tv switch socket | Nos. |  | 4 |  |  |  | 4
| Total Qty | Nos. | [5 empty] | 44
| Previous Qty | Nos. | [5 empty] | 22
| this Bill Qty | Nos. | [5 empty] | 22
l | I phase, 2 Nos x 5/15 amp, bakelite socket & switch, housed in Fabricated SS Panel suitable for hanging arrangement for Kitchen equipments. (having Two outlet /6 modular plate) | Nos. | 1
16 | Supplying, installation, Testing and commissioning flush mounting floor metallic boxes IP 66 (at terrace level) with 2 nos of 6/16A International switch & socket outlet + 1 set of blanking plate for 2 data/voice outlet suitable for AMP tyco I/o's of following modules complete with all installation kits, accessories, required to finish the installation – Sample will Approved by Client/Consultant. Cost of Switches, sockets outlet & blanking plat for Data/Voice outlets shall be included.
16.1 | 300mm x 300mm x 65/75 mm | Nos. | RO
17 | Supply, installation of temporary lighting & power arrangement for construction purpose of with industrial type switch & sockets/MCB's/ELCB's & lighting fittings as required to finish the work for interior contractor & necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules & regulations as per Airport Security Department. The material shall be taken back by the contractor. | Job | 1
| Temporary lighting and power arrangement at site | Job |  | 1 |  |  |  | 1
| Total Qty | [6 empty] | 1
| Previous Qty | [6 empty] | 1
| This Bill Qty | [6 empty] | 0
TOTAL FOR WIRING & ACCESSORIES
VI | LIGHTING FITTINGS
Installation, testing & commissioning of the following concealed / surface mounted or suspended light fixtures AS PER FINAL APPROVAL FROM ARCHITECT/CLIENT/CONSULTANT with lamps, ballast & all necessary mounting & supporting accessories. No additional cost shall be paid for supporting.
1 | FILAMENT BULB | Nos. | 46
|  | Nos. |  | 31 |  |  |  | 31
| Total Qty | Nos. | [5 empty] | 31
| Previous Qty | Nos. | [5 empty] | 31
| this Bill Qty | Nos. | [5 empty] | 0
2 | PULLEY LIGHT | Nos. | 12
|  | Nos. |  | 11 |  |  |  | 11
| Total Qty | Nos. | [5 empty] | 11
| Previous Qty | Nos. | [5 empty] | 11
| this Bill Qty | Nos. | [5 empty] | 0
3 | CHANDELIER | Nos. | 4
|  | Nos. |  | 5 |  |  |  | 5
| Total Qty | Nos. | [5 empty] | 5
| Previous Qty | Nos. | [5 empty] | 5
| this Bill Qty | Nos. | [5 empty] | 0
4 | KEG LIGHT | Nos. | 3
|  | Nos. |  | 3 |  |  |  | 3
| Total Qty | Nos. | [5 empty] | 3
| Previous Qty | Nos. | [5 empty] | 3
| this Bill Qty | Nos. | [5 empty] | 0
5 | TRACK LIGHT | Nos. | 32
|  | Nos. |  | 28 |  |  |  | 28
| Total Qty | Nos. | [5 empty] | 28
| Previous Qty | Nos. | [5 empty] | 28
| this Bill Qty | Nos. | [5 empty] | 0
6 | DECORATIVE LIGHT | Nos. | 1
|  | Nos. |  | 1 |  |  |  | 1
| Total Qty | Nos. | [5 empty] | 1
| Previous Qty | Nos. | [5 empty] | 1
| this Bill Qty | Nos. | [5 empty] | 0
7 | HANGING SPOT LIGHT | Nos. | 12
|  | Nos. |  | 31 |  |  |  | 31
| Total Qty | Nos. | [5 empty] | 31
| Previous Qty | Nos. | [5 empty] | 31
| this Bill Qty | Nos. | [5 empty] | 0
8 | LED STRIP LIGHT | Mtr. | 47
| Led Profile light | Nos. |  | 42 |  |  |  | 42
| Total Qty | Nos. | [5 empty] | 42
| Previous Qty | Nos. | [5 empty] | 42
| this Bill Qty | Nos. | [5 empty] | 0
9 | SPIKE LIGHT | Nos. | 12
| Spike light | Nos. |  | 12 |  |  |  | 12
| Total Qty | Nos. | [5 empty] | 12
| Previous Qty | Nos. | [5 empty] | 12
| this Bill Qty | Nos. | [5 empty] | 0
10 | FILAMENT LIGHT EMERGENCY | Nos. | 6
11 | HANGING SPOT LIGHT EMERGENCY | Nos. | 5
TOTAL FOR LIGHTING FIXTURES
VII | EARTHING
1 | Supply and Installation of Maintenance Free Chemical earthing using Electrode of Size approx. 38 mm dia +/- 2mm, 3 metres long bonded with 50x6 copper internal strip complete with excavation, civil works, cast iron cover with backfill compound min. 40 KG. The system shall be CPRI tested. Warranty period of chemical earthing from the date of commissioning shall be 5 years. Warranty implies the voltage between earth and neutral will not exceed 0 volts for earthing pits installed. (Note: Body earthing provided by Base builder. We have considered Neutral earthing for UPS & Server racks.) | Nos. | RO
2 | Supply & erection of G.I. strip of 50 x 6 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | RO
3 | Supply & erection of G.I. strip of 25 x 3 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | 60
4 | 1 no. 4 sq. mm YY cable in 25mm GI conduit for earthing FOR NETWORK RACK | Mtr. | 20
5 | Supplying & erecting bare copper conductor of 8 swg for earthing purpose | Mtr. | 80
7 | Supplying & erecting bare GI conductor of 8 swg for earthing purpose | Mtr.
8 | Supplying & erecting bare CU conductor of 12 swg for earthing purpose | Mtr.
9 | Supplying & installation testing & commissioning of earth terminal box | Nos.
TOTAL FOR EARTHING
VIII | MISCELLANEOUS
1 | Supply & Installation of 6A 3 pin plug top | Nos. | RO
2 | Supply & Installation of 16A 3 pin plug top | Nos. | RO
3 | Supply, installation, testing & commissioning of Cat-6 FRLS Cable for Lighting Automation | Mtr. | RO
4 | Supply & laying of Rubber Mats, CPRI tested conforming to standards like BS 921, ASTM-D 178 & IEC 479 for different operatng voltage ratings as below.
| Supply of 2M x 1M Rubber mat suitable for operatng voltage upto 1.1 KV | Set | 1
5 | Supply & fixing of approved shock treatment chart written in English and in local Language. The chart shall be framed in Teakwood and covered with glass. | Nos. | 1
6 | Supply & fixing of approved Fire Alarm evacuation plan chart written in English and in local Language approved by cleint requrements. | Nos | RO
7 | Supply & fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language | Nos. | 1
8 | Supply & handed over to client of First Aid Box | Set | RO
9 | SITC of Emergency Exit signage (battery operated) approval by client / architect / consultant. Make: Prolite or Equivalent | Nos. | RO
TOTAL FOR MISELANIOUS
IX | LOW VOLTAGE SYSTEM
A | DATA AND TELEPHONE SYSTEM
1 | Supply & Installation of 25mm.dia. GI conduit with pull box/ junction box & all accessories for DATA /VOICE/WIFI wiring as per the requirement. | Mtr. | 500
|  | Rmt |  | 1 | 25 |  |  | 25
|  | Rmt |  | 1 | 25 |  |  | 25
|  | Rmt |  | 1 | 20 |  |  | 20
|  | Rmt |  | 1 | 14 |  |  | 14
|  | Rmt |  | 1 | 20 |  |  | 20
|  | Rmt |  | 1 | 2 |  |  | 2
|  | Rmt |  | 1 | 22 |  |  | 22
|  | Rmt |  | 1 | 19 |  |  | 19
| CCTV | Rmt |  | 1 | 19 |  |  | 19
| CCTV | Rmt |  | 1 | 26 |  |  | 26
| TV | Rmt |  | 1 | 22 |  |  | 22
| Total Qty | Rmt | [5 empty] | 214
| Previous Bill | Rmt | [5 empty] | 147
| This Bill | Rmt | [5 empty] | 67
2 | Providing DATA wiring inside 25mm dia GI conduit from each Data outlet to ICT CP Point by using Indoor Type CAT6A, | Mtr. | 450
| V3 | Rmt |  | 1 | 32 |  |  | 32
| D7 | Rmt |  | 1 | 32 |  |  | 32
| D8 | Rmt |  | 1 | 32 |  |  | 32
| D1 | Rmt |  | 1 | 26 |  |  | 26
| D2 | Rmt |  | 1 | 26 |  |  | 26
| D3 | Rmt |  | 1 | 29 |  |  | 29
| D4 | Rmt |  | 1 | 29 |  |  | 29
| V1 | Rmt |  | 1 | 29 |  |  | 29
Ra-2nd
| D9 | Rmt |  | 1 | 27 |  |  | 27
| D10 | Rmt |  | 1 | 21 |  |  | 21
| D11 | Rmt |  | 1 | 10 |  |  | 10
| D12 | Rmt |  | 1 | 16 |  |  | 16
| D13 | Rmt |  | 1 | 19 |  |  | 19
| D14 | Rmt |  | 1 | 26 |  |  | 26
| D15 | Rmt |  | 1 | 36 |  |  | 36
| D16 | Rmt |  | 1 | 23 |  |  | 23
| D17 | Rmt |  | 1 | 14 |  |  | 14
| D5 | Rmt |  | 1 | 8 |  |  | 8
| D6 | Rmt |  | 1 | 8 |  |  | 8
| V2 | Rmt |  | 1 | 8 |  |  | 8
| wifi 1 | Rmt |  | 1 | 23 |  |  | 23
| wifi 2 | Rmt |  | 1 | 4 |  |  | 4
| projector | Rmt |  | 1 | 21 |  |  | 21
| CCTV | Rmt |  | 1
| Cat 6 Wiring for TV-01 | Rmt |  | 1 | 25 |  |  | 25
| Cat 6 Wiring for TV-02 | Rmt |  | 1 | 28 |  |  | 28
| Total Qty | Rmt | [5 empty] | 552
| Previous Bill | Rmt | [5 empty] | 499
| This Bill | Rmt | [5 empty] | 53
3 | Supply & Installation of Internet Jack Unit RJ-45 suitable for CAT6A | Nos. | 20
4 | Supply & Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 3 Feet | Nos. | 20
5 | Supply & Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 7 Feet | Nos. | 10
6 | Supply & laying indoors multi-pair 0.5mm dia copper PVC insulated and sheathed, armoured telephone cables on walls, ceiling, cable trays, trunking complete with clamps, cable markers etc. from MDF to the various tag blocks as specified
a | 10 pair cable armoured | Mtr. | 40
b | 5 pair cable | Mtr. | RO
c | 3 pair cable | Mtr. | RO
d. | 2 pair cable | Mtr. | RO
7 | Supply & installation of telephone tag block with KRONE terminal connectors, G.I.J.B as specified & com-plete with all interconnections and jumper connections bet-ween the two tag blocks on all floors as shown on drgs.
a | 50 pair tel. tag block | Nos. | RO
b | 20 pair tel. tag block | Nos. | 1
c | 10 pair tel. tag block | Nos. | RO
TOTAL FOR DATA AND TELEPHONE SYSTEM
GRAND TOTAL

## MB PHE
MB SHEET PHE -The Irish House RA-5th
Item No. | Description | Unit | Boq Qty | No. | Length | Width | Height | Total | Remarks
A | WATER SUPPLY PIPING
1 | CPVC Pipes conforming to ASTM D-2846, SDR-11 grade and CPVC solvent weld fittings like elbows, tees, couplars, brass threaded adaptors, insert ring etc. suitable for (domestic and flushing) cold applications rated, concealed piping within wall / floor including jointing with fittings using solvent cement, brass threaded end fittings for making connection to fixtures. The work shall also include chasing the walls with machine wherever required for concealed piping and making good the same after laying of pipes & necessary pressure testing Chasing finishing shall be done with 1:1 cement mixed mortar, restore the same original condition for internal and shaft piping, including necessary hot deep galvanised supports vertical / horizontal, as per direction of Site incharge direction. [The rate shall include supply of S.S.screws and nut bolts etc.chasing in walls done by machine] (For Domestic and Flushing water-Toilet internal) (Pipe shall be tested with 1.5 times working pressure as covered in specifications)
1.1 | 20 mm Dia | R.mt | 35
| RO Water Line on expose wall | R.mt |  | 1 | 2.08 |  |  | 2.08
| Bar area LHS wall | R.mt |  | 1 | 3.05 |  |  | 3.05
| Tap point vertical | R.mt |  | 1 | 0.27 |  |  | 0.27
| Bar Front wall | R.mt |  | 1 | 2.2 |  |  | 2.2
| Hot Water Gyser line Bar front wall | R.mt |  | 1 | 1.5 |  |  | 1.5
| RHS wall | R.mt |  | 1 | 2.3 |  |  | 2.3
| Fresh Water line main aiportline to column | R.mt |  | 1 | 1.3 |  |  | 1.3
| Column Inside vertical | R.mt |  | 1 | 2.85 |  |  | 2.85
| Above fasade glass | R.mt |  | 1 | 5.02 |  |  | 5.02
| Vertical for near glass fasade | R.mt |  | 1 | 2.85 |  |  | 2.85
| Expose main Line | R.mt |  | 1 | 2.48 |  |  | 2.48
| RHS wall vertical Line | R.mt |  | 2 | 0.45 |  |  | 0.9
| RHS wall Horizontal Line | R.mt |  | 1 | 1.44 |  |  | 1.44
Ra-2nd
| Gyser line horizontal | R.mt |  | 1 | 3.65 |  |  | 3.65
| RO outline horizontal | R.mt |  | 1 | 4 |  |  | 4
| Ro waste hprizontal | R.mt |  | 1 | 3 |  |  | 3
| Gyser line vertical | R.mt |  | 1 | 3.5 |  |  | 3.5
| RO outline vertical | R.mt |  | 1 | 3.5 |  |  | 3.5
| Ro waste vertical | R.mt |  | 1 | 3.5 |  |  | 3.5
| Total Qty. | [6 empty] | 49.39
| Previous Qty. | [6 empty] | 49.39
| This Bill | [6 empty] | 0
1.2 | 25 mm Dia | R.mt | 0
1.3 | 32mm Dia | R.mt | 0
1.4 | 40mm Dia | R.mt | 0
2 | Providing & Fixing of gun metal heavy Ball Valves-PN-16 (approved makes as covered in specification) screwed type for water system of the following diameters. Valve shall have with unions.
2.1 | 20mm Dia | Nos.
| Main line connection | Nos |  | 1 |  |  |  | 1
| RO and Gyser | Nos |  | 2 |  |  |  | 2
| Total Qty. | [6 empty] | 3
| Previous Qty. | [6 empty] | 3
| This Bill | [6 empty] | 0
2.2 | 25mm Dia | Nos. | 0
2.3 | 32mm Dia | Nos. | 0
2.4 | 40mm Dia | Nos. | 0
3 | Providing ,fixing, testing and commissioning capstan make Water Meter including providing & fixing matching Isolation valves ,strainer, non-return valve,complete with all necessary fittings etc screwed type(15Kgs/Sq.cm). Valve shall have with union.
3.1 | 20 mm Dia incoming line | Nos. | 1
3.2 | 25 mm Dia incoming line | Nos. | RO
3.3 | 32 mm Dia incoming line | Nos. | RO
4 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories
4.1 | 5 L Capacity- | Nos. | RO
4.2 | 20 L Capacity | Nos. | 1
4.3 | 35 L Capacity- For shower | Nos. | RO
5 | Supply, installation,testing & commissioning of Stiebel Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories (Optional in pantry)
5.1 | 3.5kw in pantry- optional | Nos. | RO
5.2 | 8kw | Nos. | RO
5.3 | 13kw-3ph- Subject to load permits | Nos. | RO
6 | SITC of Eco smart RO-50 with all required accessories .( Prior to order cpacaity and model to need to be confirmed by the kitchen consultant) | Nos | 1
7 | SITC of ACO grease trap -model Lipumobil 0.8 -Capacity -48 lit ( 0.8 LPS) with all required accessories ( Order shall be placed as per space available below the counter) | Nos | 0
8 | SITC of ACO grease trap -model Lipumobil S -Capacity -32 lit ( 0.5 LPS) with all required accessories | Nos | 0
B | DRAINAGE
1 | uPVC-SWR pipes conforming to IS 13592/92 including fittings conforming to IS-14935/99 and agri type pipes above 100 mm dia. conforming to IS: 4985, cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts / supported on wall / hung below slab etc. with all material & labor complete and as directed. [The Rate shall include supply and fixing of hotdip galvanised bracket nut bolts/ PVC Coated U-Clamp and screws] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] (For Soil , Waste, Vent and RWP-Internal and vertical shaft ).
1.1 | 40mm Dia | R.mt | 2
1.2 | 50mm Dia | R.mt | 6
1.3 | 65mm Dia | R.mt | 0
1.4 | 75mm Dia | R.mt | 7
| Trap to small GT line | R.mt |  | 1 | 0.7 |  |  | 0.7
|  | R.mt |  | 1 | 0.55 |  |  | 0.55
|  | R.mt |  | 1 | 0.83 |  |  | 0.83
|  | R.mt |  | 1 | 0.58 |  |  | 0.58
|  | R.mt |  | 1 | 0.6 |  |  | 0.6
|  | R.mt |  | 1 | 1.45 |  |  | 1.45
| Trap to main GT line | R.mt |  | 1 | 2.05 |  |  | 2.05
| 600x300 to 600x600 main GT line | R.mt |  | 1 | 0.8 |  |  | 0.8
| 300x300 to 600x600 main GT line | R.mt |  | 1 | 0.4 |  |  | 0.4
| Total Qty. | [6 empty] | 7.96
| Previous Qty. | [6 empty] | 7.96
| This Bill | [6 empty] | 0
1.5 | 100 mm Dia | R.mt | 2
1.6 | 150 mm Dia | R.mt | RO
2 | Supply, Install PVC Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 2
| Floor trap | Nos. |  | 6 |  |  |  | 6
| Total Qty. | [6 empty] | 6
| Previous Qty. | [6 empty] | 6
| This Bill | [6 empty] | 0
3 | Supply, Install PVC Multi Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 4
4 | Supply, Install PVC urinal Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0
5 | Supply, Install PVC P- Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0
C | SANITARY AND C. P. FITTINGS & FIXTURES
Only installation, testing and commissioning of sanitary and C.P. fittings
1.1 | EWC with seat cover | Nos | 0
1.2 | Concealed flush tank | Nos | 0
1.3 | Concealed flush valve | Nos | 0
1.4 | Health Faucet | Nos | 0
1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 0
1.6 | Bided | Nos | R.O.
1.7 | Under Counter Wash Basin including waste Coupling | Nos | 0
1.8 | Wash Basin Cock | Nos | 0
1.9 | shower and mixer | Nos | 0
1.1 | Jet Spray | Nos | 0
1.11 | Bath Tub including waste Coupling and nessessary connections | Nos | 0
1.12 | Under Counter Sink including waste Coupling | Nos | 1
1.13 | Sink Pillar Cock | Nos | 1
| Sink Pillar cock | Nos |  | 2 |  |  |  | 2
| Total Qty. | [6 empty] | 2
| Restricted Qty | [6 empty] | 1
| Previous Qty. | [6 empty] | 2
| This Bill | [6 empty] | 0
1.14 | Bottle Trap for WHB/ sink and urinal with all connecting pipes | Nos | 1
| Connection pipes | Nos | 1 | 2 |  |  |  | 2
| Total Qty. | [6 empty] | 2
| Restricted Qty | [6 empty] | 1
| Previous Qty. | [6 empty] | 2
| This Bill | [6 empty] | 0
1.15 | Angle Cock with PVC pipe connection upto WHB/sink/Geyser connection | Nos | 7
| Bar area | Nos | 1 | 7 |  |  |  | 7
| For Ro and Gyser above ceiling | Nos | 1 | 3 |  |  |  | 3
| Total Qty. | [6 empty] | 10
| Previous Qty. | [6 empty] | 10
| This Bill | [6 empty] | 0
1.16 | Urinal | Nos | 0
1.17 | Auto Flush Valve & Sensor with connecting piping & spreader for urinal(DC) | Nos | 0
D | S.S. GRATING
Only installations/ testing and commissioning of S.S.Gratings
1 | Making chamber in brick work including internal tiling etc for S.S Grating size, 1200mm x 200mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 0
2 | Making chamber in brick work including internal tiling etc for S.S Grating size, 600mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 1
| Floor greeting size 300x600 | Nos |  | 1 |  |  |  | 1
| Total Qty. | [6 empty] | 1
| Previous Qty. | [6 empty] | 1
| This Bill | [6 empty] | 0
4 | Making chamber in brick work including internal tiling etc for S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 3
| Floor greeting size 300x300 | Nos |  | 2 |  |  |  | 2
| Floor greeting size 500x500 | Nos |  | 1 |  |  |  | 1
| Total Qty. | [6 empty] | 3
| Previous Qty. | [6 empty] | 3
| This Bill | [6 empty] | 0

## MB HVAC
MB HVAC RA-5th
Item No. | Description | Unit | Boq Qty | No. | Length | Width | Height | Total | Remarks
1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) :
1.1 | CEILING SUSPENDED AHU :
Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications:
Frame Structure: It shall consist of 48mm Extruded Aluminium with thermal break profile.
Panel: 45mm +/- 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg/m3 or PUF insulation of 48 kg/m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI.
Filtration Section: It shall be provided with single stage washable type of prefilter 'MERV 8' first stage which shall be placed before coil section.
Coil Section: Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m/sec (500 fpm).
Drain Pan: Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation.
Fan Section: SISW / DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration.
Other Details : AHU to house control box/ terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over/ Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers / Fire Alarm Panel. Power cable from Terminal box to motor & control cabling of required size upto the thermostat / sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports & accessories required for installation.
Contractor shall design the chilled water coil according to the following conditions:
a. Coil air entering temperature - 75.4°F DB
b. Coil air leaving temperature - 54 deg. F DB/ 52.99 deg. F WB
c. Chilled water temperature entering - 6.0 deg. C/ 42.8 deg. F
d. Chilled water temperature leaving - 13.3 deg. C/ 55.9 deg. F
Make : VTS / Zeco / Citizen
Type Capacity Tonnage ESP No. of
(Cfm) TR (mm WG) Rows
a | CS AHU 2500 9.2 25 4/6
GENERAL NOTES:
a. | LHS & RHS VALVE station location to be confirmed.
b. | Fan outlet velocity - 1600 FPM
c. | Contractor shall submit static pressure calculation for all above units to Client/Consultant.
d. | Any change in motor HP shall be made at no extra cost to client.
e. | Fan efficiency shall be minimum 75%
f. | The cost shall be included liftting & shifting of each equipment / material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material / equipment.
2 | CHILLED WATER PIPING WITH INSULATION:
2.1 | CHW PIPE
SITC of MS Heavy duty class 'C' ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker/ paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. "Table E" of BS code for flange thickness to be adhered.
Make: Jindal Hissar / TATA
a | Φ 65 mm | Rmt | 110
| Φ 40 mm | Rmt | 30
| 40 mm Inlet line AHU-1 | Rmt |  | 1 | 3.28 |  |  | 3.28
| 40 mm outlet line AHU-1 | Rmt |  | 1 | 3.28 |  |  | 3.28
| 40 mm Inlet line AHU-2 | Rmt |  | 1 | 3.28 |  |  | 3.28
| 40 mm outlet line AHU-2 | Rmt |  | 1 | 3.28 |  |  | 3.28
| Total Qty | Rmt | [5 empty] | 13.12
| Previous Qty | Rmt | [5 empty] | 13.12
| This Bill | Rmt | [5 empty] | 0
2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE
SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class "O" Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports.
Make: Armaflex & K-flex
a | Φ 65 mm | Rmt | 110
| Φ 40 mm | Rmt | 30
| 40 mm Inlet line AHU-1 | Rmt |  | 1 | 3.28 |  |  | 3.28
| 40 mm outlet line AHU-1 | Rmt |  | 1 | 3.28 |  |  | 3.28
| 40 mm Inlet line AHU-2 | Rmt |  | 1 | 3.28 |  |  | 3.28
| 40 mm outlet line AHU-2 | Rmt |  | 1 | 3.28 |  |  | 3.28
| Total Qty | Rmt | [5 empty] | 13.12
| Previous Qty | Rmt | [5 empty] | 13.12
| This Bill | Rmt | [5 empty] | 0
2.3 | BALL VALVE
SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure: Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
Make: Zoloto / Audco / Kitz
a | Φ 40 mm | Nos. | 8
| Ball Valve |  |  | 8 |  |  |  | 8
| Total Qty | Nos. | [5 empty] | 8
| Previous Qty | Nos. | [5 empty] | 8
| This Bill | Nos. | [5 empty] | 0
2.4 | BALL VALVE WITH Y-STRAINER
SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure: Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation.
Make: Zoloto / Audco / Kitz
a | Φ 40 mm | Nos. | 2
| Ball Valve Y-Strainer |  |  | 2 |  |  |  | 2
| Total Qty | Nos. | [5 empty] | 2
| Previous Qty | Nos. | [5 empty] | 2
| This Bill | Nos. | [5 empty] | 0
2.5 | PIBCV VALVES
SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with +/- 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal / POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
Make: Oventrop / Siemens / Danfoss
a | Φ 40 mm | Nos. | 2
| PIBCV VALVES |  |  | 2 |  |  |  | 2
| Total Qty | Nos. | [5 empty] | 2
| Previous Qty | Nos. | [5 empty] | 2
| This Bill | Nos. | [5 empty] | 0
2.6 | Auto Air Vent Valves
Make: Anergy / Flamco
Providing and fitting Auto Vent Valves.
a | SITC of Auto air vent in each risers & common headers & AHU. 3/4" auto vent valves at each coil / riser/ header. | Nos. | 4
| Air Vent |  |  | 4 |  |  |  | 4
| Total Qty | Nos. | [5 empty] | 4
| Previous Qty | Nos. | [5 empty] | 4
| This Bill | Nos. | [5 empty] | 0
2.7 | SITC of Pressure gauges & Thermometers
Make: H Guru / Waree
Necessary pressure gauges and thermometers 4" Dial type.
a | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg/CM2 | Nos. | 4
| Pressure Gauge |  |  | 4 |  |  |  | 4
| Total Qty | Nos. | [5 empty] | 4
| Previous Qty | Nos. | [5 empty] | 4
| This Bill | Nos. | [5 empty] | 0
b | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9/12 inches, Thermometer, Range 0-50 deg C | Nos. | 4
| Thermometers |  |  | 4 |  |  |  | 4
| Total Qty | Nos. | [5 empty] | 4
| Previous Qty | Nos. | [5 empty] | 4
| This Bill | Nos. | [5 empty] | 0
c | Thermowells | Nos. | 8
| Thermowells |  |  | 8 |  |  |  | 8
| Total Qty | Nos. | [5 empty] | 8
| Previous Qty | Nos. | [5 empty] | 8
| This Bill | Nos. | [5 empty] | 0
d | SITC of Brass Test Plug of industrial grade mounting on water | Nos. | RO
2.8 | INSULATED CONDENSATE DRAIN PIPE
SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees & reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
Make: Supreme, Prince, Astral
a | Φ 25 mm | Rmt | 10
| AHU-1 |  |  | 1 | 6.61 |  |  | 6.61
| AHU-2 |  |  | 1 | 7.9 |  |  | 7.9
| Total Qty | Rmt | [5 empty] | 14.51
| Restricted Qty. | Rmt | [5 empty] | 10
| Previous Qty | Rmt | [5 empty] | 14.51
| This Bill | Rmt | [5 empty] | 0
b | Φ 32 mm | Rmt | 20
NOTES FOR PIPING:
a | Cover all open pipe ends with muslin cloth during construction
b | Pipe cleaning & chemical treatment as per specs shall be included in the piping cost.
c | Unit rates for all indicated sizes of pipes & valves shall be furnished.
d | Cleaning/Painting of pipe before insulation shall be included in piping cost.
e | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant.
f | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
SUB-TOTAL
3 | SHEET METAL WORKS:
3.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
a | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | RO
b | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 10
c
d | FACTORY FABRICATED G.I FLAT OVAL DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Exposed Flat Oval ducting, Elbows with turning vanes, Splitters, Reducers, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. All exposed ducts has to be powder coated by HVAC contractor, sample and color code to be presented for the validation of Client / Architect.
3.2 | GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
| 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | RO
| 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 115
| 850x300 mm duct | sqm |  | 1 | 14.2 | 2.3 |  | 32.66
| 850x300 mm duct Glass screen side | sqm |  | 1 | 13.6 | 2.3 |  | 31.28
| 550x200 mm duct | sqm |  | 2 | 6 | 1.5 |  | 18
| 550x200 mm counter area | sqm |  | 1 | 2.56 | 1.5 |  | 3.84
| Bar counter area | sqm |  | 1 | 1.8 | 1.5 |  | 2.7
| Total Qty in sqm | [6 empty] | 88.48
| Previous Qty | [6 empty] | 88.48
| This Bill Qty | [6 empty] | 0
3.3 | EXTRUDED ALUMINIUM CEILING GRILLES
Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square/rectangular/Linear). The grilles shall be with 15/30/45° deflections as per requirement. The Colour shall be decided and approved by client and architect.
| Curve Grille | Sq.mtr | 1.5
Make: Cosmos, Air Master & System Air
| Grill | sqm |  | 15 | 0.4 | 0.1 |  | 0.6
| Side Throw Curved Grill | Sqm |  | 12 | 0.4 | 0.1 |  | 0.48
| Total Qty | [6 empty] | 1.08
| Previous Qty | [6 empty] | 1.08
| This Bill Qty | [6 empty] | 0
3.4 | SPIGOT DAMPER FOR ELLIPTICAL DUCT
| Supply, installation and testing of galvanized steel construction dampers for circular ducts ( VCD ) within ducts provided with suitable lever and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | Sq.mtr | 0.5
Make: Cosmos, Air Master & System Air
| SPIGOT Damper | Sqm |  | 1 | 1 |  |  | 1
| Total Qty | Sqm | [5 empty] | 1
| Restricted qty | Sqm | [5 empty] | 0.5
| Previous Qty | Sqm | [5 empty] | 1
| This Bill Qty | Sqm | [5 empty] | 0
3.5 | OPPOSED BLADE DAMPER
| SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 1.5
| Grill damper | sqm |  | 15 | 0.4 | 0.1 |  | 0.6
| Side Throw Curved Grill Damper | Sqm |  | 12 | 0.4 | 0.1 |  | 0.48
| Total Qty | Sqm | [5 empty] | 1.08
| Previous Qty | Sqm | [5 empty] | 1.08
| This Bill Qty | Sqm | [5 empty] | 0
3.6 | CANVAS CONNECTION
a | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
b | For AHU | Nos. | 2
| Canvas connection | Nos. |  | 2 |  |  |  | 2
| Total Qty | Nos. | [5 empty] | 2
| Previous Qty | Nos. | [5 empty] | 2
| This Bill Qty | Nos. | [5 empty] | 0
3.7 | CURTAIN TYPE FIRE DAMPER
SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 / 225°F, etc; as per the approved shop drawings and specifications.
Make: Carryaire / System Air / Dynacraft / Air Master
a | Bare fire dampers | Sq.mtr | 0.5
b | Fusible link as per specification UL 555 | No | 1
NOTES:
The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
Muslin cloth cover for all air outlets during construction.
Pressure testing of complete duct work as per DW/ SMACNA standard.
Silicon sealant for longitudinal & transverse joints as per specification.
Diffusers & grilles shall be powder coated as per color approved by Architect.
SUB-TOTAL
4 | THERMAL & ACOUSTIC INSULATION:
4.1 | THERMAL INSULATION
| Supply & fixing of Thermal insulation for supply air duct using 13mm thick class " O " Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 100
Make: Armaflex & K-flex
| 850x300 mm duct | sqm |  | 1 | 14.2 | 2.3 |  | 32.66
| 850x300 mm duct Glass screen side | sqm |  | 1 | 13.6 | 2.3 |  | 31.28
| 550x200 mm duct | sqm |  | 2 | 6 | 1.5 |  | 18
| 550x200 mm counter area | sqm |  | 1 | 2.56 | 1.5 |  | 3.84
| Total Qty in sqm | Sqm | [5 empty] | 85.78
| Previous Qty | Sqm | [5 empty] | 85.78
| This Bill Qty | sqm | [5 empty] | 0
4.2 | ACOUSTIC INSULATION
| Supply & fixing acoustic insulation for ducting using Class "1" closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal & transverse joints sealed with adhesive in neat & clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W/(m.K) and density of 140 - 180 kg/m³. | Sq.mtr | 25
Make: Armaflex & K-flex
| AHU and Duct Mouth connection | sqm |  | 2 | 0.3 | 2.3 |  | 1.38
| Total Qty in sqm | sqm | [5 empty] | 1.38
| Previous Qty | sqm | [5 empty] | 1.38
| This Bill Qty | Sqm | [5 empty] | 0
Note:
a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
c. | Thermal insulation shall be internal for Elliptical / Expossed ducting.
SUB-TOTAL
5 | ELECTRICAL WORKS:
5.1 | STARTER PANEL
SITC of indoor / outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP & BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB/MCCB, Contactor, Bi-metal O/L relay with SPP, ON/OFF Push buttons, on / off / trip indication Lamp, on off push button, & phase indication Lamp. Selection of relay, contractor, MPCB/MCCB etc. as per Type-2 Coordination. Panel shall have provision to connect with BMS.
a | Suitable for 2500 CFM AHU, DOL Starter Panel | Nos. | 2
| AHU Stater | Nos. |  | 2 |  |  |  | 2
| Total Qty in nos | Nos. | [5 empty] | 2
| Previous Qty | Nos. | [5 empty] | 0
| This Bill Qty | Nos. | [5 empty] | 2
6.2 | POWER CABLING
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium /Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners/ Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
a | Suitable Power Cable:
| Suitable for 2500 CFM AHU, DOL Starter Panel | Rmt | 10
| AHU Stater | rmt |  | 2 | 20.5 |  |  | 41
| Total Qty in nos | Nos. | [5 empty] | 41
| Previous Qty | Nos. | [5 empty] | 41
| This Bill Qty | Nos. | [5 empty] | 0
b | Earthing:
| 8 SWG | Rmt | 20
6.3 | BTU METER
Supply,fixing and testing of inline Btu meter for the flow rate & temperature measurement consisting mainly of following 3 parts
a) Ultrasonic Flow Meter
b) Matched pair of temp sensor
c) Flowcell Sensor
c) BTU Meter - 4 - 20mA DC from flowmeter
Insertion type flowmeter shall be suitable for chilled water application for temp. Ranging from 0 to 50 deg C. Power supply shall be 240V AC (+/-) 15 %. Display shall have 16 characters LCD display with Back light, flow rate, Velocity, totaliser etc. Output shall be BMS Modbus compatible & shall have keypad lockout security option. It also should be able to show various units such as gallons, ft^3, lbs, liters, m^3, kg etc
Make: Honeywell / Danfoss / Siemens
a | Dia 65 mm | No. | 1
6.4 | CABLE TERMINATION :
Supply & Making of Cable termination of armoured / unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY & copper for 2XFY & YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing & commissioning of cables, meggaring values & submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools & dies shall be arranged by contractor.
a | Suitable for 2500 CFM AHU | Nos. | 4
| CABLE TERMINATION : | rmt |  | 4 |  |  |  | 4
| Total Qty in nos | Nos. | [5 empty] | 4
| Previous Qty | Nos. | [5 empty] | 4
| This Bill Qty | Nos. | [5 empty] | 0
6.5 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports.
a | 50mm wide | Rmt | 10

## MB Fire Fighting
MB Sheet Fire Fighting -The Irish House RA-5th
Item No. | Description | unit | Boq qty | No. | Length | Width | Height | Total | Remarks
1 | Providing, laying, jointing, testing and commissioning of G.I. `C' Class pipes (IS:1239 (Part-I)-1979) including cutting,threading welding etc providing all malleable galvanized iron fittings conforming to IS 1879, viz. Flanges, bends, tees, elbows,reducers, unions, supporting with G. I. clamps, hangers, M.S. brackets etc. including cutting holes and chases in brick or RCC wall / slabs and making good the same to the Approval of Architect / consultant,complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade. ( Note- Rigid pipe extension from existing line is considered)
i) | 25 mm dia. | RMT | 18
| Branch -1 above Bar counter | RMT |  | 1 | 4 |  |  | 4
| Sprinklar branch bar area | RMT |  | 2 | 0.895 |  |  | 1.79
| Branch -2 above rafters | RMT |  | 1 | 1.11 |  |  | 1.11
| Sprinklar brances | RMT |  | 1 | 2.685 |  |  | 2.685
| Sprinklar brances | RMT |  | 1 | 1.095 |  |  | 1.095
|  | RMT |  | 1 | 1.3 |  |  | 1.3
|  | RMT |  | 1 | 0.895 |  |  | 0.895
| Above hut both side line | RMT |  | 2 | 4.135 |  |  | 8.27
| 3 rd branc above C- bench sofa | RMT |  | 1 | 6 |  |  | 6
|  | RMT |  | 1 | 3 |  |  | 3
| Total Qty in Rmt. | [6 empty] | 30.145
| Previous bill qty. |  |  |  |  | 30.145 |  | 30.145
| This bill qty. | [6 empty] | 0
ii) | 32 mm dia. | RMT | 0
iii) | 40 mm dia. | RMT | 3
| Branch -1 above Bar counter | RMT |  | 1 | 2.02 |  |  | 2.02
|  | RMT |  | 1 | 0.79 |  |  | 0.79
| Branch -2 above rafters | RMT |  | 1 | 0.815 |  |  | 0.815
| Above hut both side line | RMT |  | 2 | 1.32 |  |  | 2.64
|  | RMT |  | 2 | 2.08 |  |  | 4.16
| 3 rd branc above C- bench sofa | RMT |  | 1 | 2.055 |  |  | 2.055
|  | RMT |  | 1 | 0.83 |  |  | 0.83
| Total Qty in Rmt. | [6 empty] | 13.31
| Previous bill qty. | [6 empty] | 13.31
| This bill qty. | [6 empty] | 0
iv) | 50 mm dia. | RMT | 10
| Branch -2 above rafters | RMT |  | 1 | 5.225 |  |  | 5.225
| 3 rd branc above C- bench sofa | RMT |  | 1 | 4.82 |  |  | 4.82
| Total Qty in Rmt. | [6 empty] | 10.045
| Previous bill qty. | [6 empty] | 10.045
| This bill qty. | [6 empty] | 0
v) | 65 mm dia. | RMT | 5
| Airport chilled line to main Header | RMT |  | 1 | 5.5 |  |  | 5.5
| Down | RMT |  | 1 | 0.6 |  |  | 0.6
| Main Header run | RMT |  | 1 | 5.25 |  |  | 5.25
| Total Qty in Rmt. | [6 empty] | 11.35
| Previous bill qty. | [6 empty] | 11.35
| This bill qty. | [6 empty] | 0
vi) | 80 mm dia. | RMT | 0
vii) | 100 mm dia. | RMT | 0
2 | Providing , fixing testing and commissioning of pendant type sprinkler heads 68 deg. Temp.(Quick response type) | No. | 0
3 | Providing , fixing testing and commissioning of concealed type sprinkler heads 68 deg. Temp.(Extended coverage /Quick response type) | No. | 0
4 | Providing , fixing testing and commissioning of upright type sprinkler heads 68 deg. temp(Quick response type)- Optional Subject to liasion team requirements | No. | 0
5 | Providing , fixing testing and commissioning of upright type sprinkler heads 79 deg. Temp (Quick response type) | No. | 12
| Sprinkler | No. |  | 26 |  |  |  | 26
| Total Qty in Rmt. | no | [5 empty] | 26
| Previous bill qty. | no | [5 empty] | 26
| This bill qty. | no | [5 empty] | 0
6 | Providing & fixing testing and commissioning of braided UL Rated SS Flexible pipe
i) | 1 MT Long | No. | 0
ii) | 1.6 MT Long | No. | 12
7 | Gun metal chrome finished Ball valves (PN 16) with fittings of screwedend type.
I) | 40 mm dia. | No. | R.O.
I) | 32 mm dia. (Sprinkler drain-OPTIONAL) | Nos. | 1
8 | Butterfly Valves (PN 16) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification & to the level of satisfaction of Site- Incharge.
I) | 150 mm dia. | No. | R.O.
I) | 100 mm dia. | No. | R.O.
I) | 65 mm dia. (OPTIONAL) | No. | 2
| Main Header connection 2 nos. | Nos. |  | 1 | 2 |  |  | 2
| Total Qty in Rmt. | [6 empty] | 2
| Previous bill qty. | [6 empty] | 2
| This bill qty. | [6 empty] | 0
9 | 6kg capacity ABC type dry chemical powder fire Extinguishers with wall mounting brackets | Nos. | 4
| AbC Type fire extingusher | No. |  | 4 |  |  |  | 4
| Total Qty in Rmt. | no | [5 empty] | 4
| Previous bill qty. | no | [5 empty] | 4
| This bill qty. | no | [5 empty] | 0
10 | 6kg capacity K type fire Extinguishers with wall mounting brackets | No. | 0
11 | 5kg capacity CO2 type fire Extinguishers with wall mounting brackets | No. | 2
| co2 Type fire extingusher | No. |  | 2 |  |  |  | 2
| Total Qty in Rmt. | no | [5 empty] | 2
| Previous bill qty. | no | [5 empty] | 2
| This bill qty. | no | [5 empty] | 0
12 | 9Lit AR-AFFF type fire Extinguishers with wall mounting brackets | Nos. | R.O.
13 | Flow switch on sprinkler distribution header on each floor with 2 SPDT contacts suitably rated, capable of the high pressure system and connected to fire alarm panel through cable.
i) | 100 mm dia. | No. | 0
14 | Ceasefire 5 Kg Ceiling Mounted Fire Extinguisher Clean Agent FE-36, Zero ODP, Stored Pressure Type, Pressure Gauge, Gross Weight 7.7 Kg, empty Weight 2.7 Kg, Can Height 264MM, Diameter 240MM,Discharge Time less than 8 Secs, Auto discharge mechanism on temperature rise, applicable on Class A,B,C and electrically started Fire, Can Construction : Deep drawn & Co2 Mig welded, Valve Construction : Forging & Machining, Internal Coating of Can : Epoxy Powder coating, External Coating of Can : Epoxy Polyster Powder coating, Sheet metal thickness : 2.0MM, Helium Leak Detection Test, 5 Years Warranty-model no 1CH21CF | No. | 0

## MB FIRE ALARM
MB Sheet Fire Alarm System -The Irish House RA-5th
SR.NO | DESCRIPTION | UNIT | Boq Qty. | No. | Length | Width | Height | Total | Remarks
A | ADDRESSABLE FIRE ALARM SYSTEM - NOTIFIER MAKE
1 | Analog Addressable Fire Alarm Control panel with battery back up for 24 hours normal operation and 15 minutes alarm operation. The control panel, battery charger etc. The panel shall be with 1 loop and expandable upto 2 loop capacity. The Fire Alarm Control Panel shall include a full featured operator interface control and annunciation panel that shall include a backlit 640-character liquid crystal display, individual, color coded system status LEDs, and a QWERTY style alphanumeric keypad for the field programming and control of the fire alarm system. Number of Loops / Fire alarm panels should be worked out based on loop capacity, It shall be selected keeping atlest 20 addresses as spare capacity in each loop. The control panel shall be capable of network expandable upto multiple panels. The panel & all devises should be FM approved and comply UL 864 or equivalent. The enclosure shall also be UL listed or equivalent The quoted rate shall include supply of necessary software and harware for progamming the panel with all necessary licence. Should have the Facility to get integrated with the MAIN FAS Panel of the Building. Electrical main LT panel, (PRO).Connecting to BMS on Bacnet or TCP/IP. | Nos | RO
i) Each loop with Min. 125 Devices & Detectors modules connection capability of Addressable FACP) 2 Loop Panel.
ii) FACP with all in-built modules & displays.
iii) 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working.
iv) Programming & setting up
v) system to be capable of operating the system for 2 hours during an emergency condition including all necessary software for remote programming of fire alarm system through central control station.
2 | Passive Repeater Panel with 80-Character (2x40) display with supervised power supply from FACP. Repeater Panel shall monitor and control (Scroll, Acknowledge, Reset & Mute) all the events of the FACP to which it is connected and it shall have Port Vectoring / Event Filtering capability of showing only ALARMS, TROUBLES or SUPERVISORY or customized combinations of user selected events. | Nos | RO.
2.1 | Supply installation and testing of signal loop components in a suitable galvanised steel junction box. | Nos. | 1
3 | Detectors and Devices
3.1 | Supply,Installation,Testing & Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices & shall be capable of providing DPDTcontact rated at 24V DC, 2A. | Nos | 2
| Monitor modulaue |  |  | 2 |  |  |  | 2
| Total Qty | Nos | [5 empty] | 2
| Previous Bill | Nos | [5 empty] | 2
| This Bill | Nos | [5 empty] | 0
3.2 | Supply,Installation,Testing & Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system and shall be capable of providing DPDTcontact rated at 24v DC, 2A. | Nos | 2
| Relay Moudule |  |  | 2 |  |  |  | 2
| Total Qty | Nos | [5 empty] | 2
| Previous Bill | Nos | [5 empty] | 2
| This Bill | Nos | [5 empty] | 0
3.3 | Supply,Installation,Testing & Commissioning of wall / ceiling mounted Horn cum Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication and necessary accessories including back box. | Nos | 2
| Horn |  |  | 2 |  |  |  | 2
| Total Qty | Nos | [5 empty] | 2
| Previous Bill | Nos | [5 empty] | 2
| This Bill | Nos | [5 empty] | 0
3.5 | Supply,Installation,Testing & Commissioning of above / below ceiling mounted Analogue Addressable Flash scan Type Photoelectric smoke detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 6
| Smoke Detector |  |  | 6 |  |  |  | 6
| Total Qty | Nos | [5 empty] | 6
| Previous Bill | Nos | [5 empty] | 6
| This Bill | Nos | [5 empty] | 0
3.6 | Supply,Installation,Testing & Commissioning of above / below ceiling mounted Analogue Addressable Heat / Thermal detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 1
| Heat Detector |  |  | 1 |  |  |  | 1
| Total Qty | Nos | [5 empty] | 1
| Previous Bill | Nos | [5 empty] | 1
| This Bill | Nos | [5 empty] | 0
3.7 | Supply,Installation,Testing & Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressabla module that monitors and reports contact status. | Nos | 2
| Call point |  |  | 2 |  |  |  | 2
| Total Qty | Nos | [5 empty] | 2
| Previous Bill | Nos | [5 empty] | 2
| This Bill | Nos | [5 empty] | 0
4 | Response indicator. | Nos | RO
NOTE: FIRE PANEL SHALL BE PROVIDED WITH FACILITY TO INTEGRATE WITH AIRPORT PANEL
5 | CABLES
Supplying, laying, testing and commissioning of 1100V grade FIRE RESISTANCE LOW SMOKE multicore, round type, insulated, sheathed, flexible copper conductor control cables with Including necessary end terminations with copper lugs, junction box, crimping identification tags at each end etc.,) RED COLOUR ONLY (MAKE: RR CABLE)
a | 2 core x 1.5 Sq.mm armoured cable(Un-screened, LSZH armoured) | Mtr | 220
| ceiling Looping Cable | mtr |  | 55 |  |  |  | 55
| Total Qty | Mtr | [5 empty] | 55
| Previous Bill | Mtr | [5 empty] | 55
| This Bill | Mtr | [5 empty] | 0
6 | REWORKS
Shifting , relocation and reworking including extending of cable & testing and commissioning of the following devices
a | Photoelectric Smoke Detectors (BFC) at actuals. | Nos. | R.O.
b | Response Indicator of AFC detectors at actuals | Nos. | R.O.

## MB CCTV
MB SHEET CCTV FOR The Irish House RA-5th
SR.NO | DESCRIPTION | UNIT | Boq Qty. | No. | Length | Width | Height | Total | Remarks
II | CCTV SURVIELLIANCE SYSTEM
1 | Supply, Istallation, Testing & Commissioning of 5MP HD Dome Camera Model No. DS-2CE76HOTITMFS | Nos. | 7
| Camera |  |  | 8 |  |  |  | 8
| Total Qty | Nos | [5 empty] | 8
| Previous Qty | Nos | [5 empty] | 8
| this Bill Qty | Nos | [5 empty] | 0
2 | Supply & Installation of 230/12V -20A DC Power Supply Unit for Camera Make: MRE/ACOORD | Set | 1
| Camera |  |  | 1 |  |  |  | 1
| Total Qty | Nos | [5 empty] | 1
| Previous Qty | Nos | [5 empty] | 1
| this Bill Qty | Nos | [5 empty] | 0
3 | 4-Channel Embedded DVR, Real Time Recording @ CIF Resolution for all Channels or D1 Resolution on 1st Channel and rest at Real Time @ CIF , Support English OSD, 1 SATA slot available, 230VAC & TCP/IP Connectivity. (Honeywell Make, HDDVR1004 Model) | Nos
4 | 8-Channel Embedded DVR, Real Time Recording @ CIF Resolution for all Channels or D1 Resolution on 1st Channel and rest at Real Time @ CIF , Support English OSD, 1 SATA slot available, 230VAC & TCP/IP Connectivity. (Honeywell Make, HDDVR1008 Model) | Nos | 1
| DVR |  |  | 1 |  |  |  | 1
| Total Qty | Nos | [5 empty] | 1
| Previous Qty | Nos | [5 empty] | 1
| this Bill Qty | Nos | [5 empty] | 0
5 | VGA Flat screen TFT 21" high resolution Monitor with power supply complete | No. | RO
6 | 8 TB Hard Disk (15 Days) | No. | 1
| DVR |  |  | 1 |  |  |  | 1
| Total Qty | Nos | [5 empty] | 1
| Previous Qty | Nos | [5 empty] | 1
| this Bill Qty | Nos | [5 empty] | 0
| Supply & Instllation of Power connector | No. | 7
| DVR |  |  | 8 |  |  |  | 8
| Total Qty | Nos | [5 empty] | 8
| Previous Qty | Nos | [5 empty] | 8
| this Bill Qty | Nos | [5 empty] | 0
| Supply & Installation of co-axial connector | No. | 14
| DVR |  |  | 16 |  |  |  | 16
| Total Qty | Nos | [5 empty] | 16
| Previous Qty | Nos | [5 empty] | 16
| this Bill Qty | Nos | [5 empty] | 0
7 | Supply & laying of 2C x 1.5 sq. mm non-FRLS flexible PVC insulated cable with GI conduit FOR POWER SUPPLY | Mtr | 245
8 | Supply & laying of RT-3 Co-axial & Power FRLS Cable | Mtr | 245
| cctv cable | Rmt |  | 1 | 26 |  |  | 26
|  | Rmt |  | 1 | 25 |  |  | 25
|  | Rmt |  | 1 | 21 |  |  | 21
|  | Rmt |  | 1 | 14 |  |  | 14
|  | Rmt |  | 1 | 10 |  |  | 10
|  | Rmt |  | 1 | 33 |  |  | 33
|  | Rmt |  | 1 | 30 |  |  | 30
|  | Rmt |  | 1 | 23 |  |  | 23
|  | Rmt |  | 1 | 20 |  |  | 20
| Total Qty | [6 empty] | 202
| Previous Qty | [6 empty] | 202
| This Bill qty | [6 empty] | 0
9 | Supply & Laying of 25mm dia. GI Conduit | Mtr | 90
| GI Conduit | Rmt |  | 1 | 19 |  |  | 19
|  | Rmt |  | 1 | 26 |  |  | 26
| Total Qty | [6 empty] | 45
| Previous Qty | [6 empty] | 45
| This Bill qty | [6 empty] | 0
10 | Supply & laying of RG6 cable for video transmission from all cameras to DVR located in Server Room with PVC conduit. | Mtr | RO

## MB PA System
Thr Irish House @ LUCKNOW RA-5th
PA SYSTEM BOQ
SR. No | DESCRIPTION | UNIT | Boq Qty. | No. | Length | Width | Height | Total | Remarks
A | PA/MUSIC SYSTEM EQUIPMENTS SUPPLY
1 | Supply & Installation of JBL make Loudspeaker (6 watt) CEILING SPKR to match with Airport PA System | Nos. | 8
2 | Supply of JBL make Loudspeaker 20 watt wall mount SPKR | Nos.
3 | Supply, installation, testing & commissioning of Control 24CT Microplus JBL make Speakers | Nos. | RO
4 | Supply of Amplifier with Line matching transformers | Nos. | RO
5 | Supply of DSP with Card Model No. BLU-100/BLU 102 | Nos. | RO
6 | Supply of ZONE CONTROLLER Model No. BLU-3 | Nos. | RO
7 | Supply of Paging Mic Model No. DST-995 | Nos. | RO
8 | Supply of DVD Player for BGM | Nos. | RO
9 | Supply & Laying of 2x2.5 Sq.mm FRLS Speaker Cable. The cost of conduit shall be paid separately. | Mtr. | 72
| DB extra | Rmt. |  | 1 | 1.5 |  |  | 1.5
| DB to Ceiling level | Rmt. |  | 1 | 3 |  |  | 3
| Ceiling to rafter | Rmt. |  | 1 | 4.2 |  |  | 4.2
| Ceiling to rafter down | Rmt. |  | 1 | 1.6 |  |  | 1.6
| Long rafter | Rmt. |  | 1 | 9.2 |  |  | 9.2
| Rafter to center rafter | Rmt. |  | 1 | 3 |  |  | 3
| Center rafter | Rmt. |  | 1 | 7.2 |  |  | 7.2
| Center rafter return | Rmt. |  | 1 | 7.2 |  |  | 7.2
| center rafter to corner rafter | Rmt. |  | 1 | 3 |  |  | 3
| Long rafter 2nd | Rmt. |  | 1 | 9.2 |  |  | 9.2
| 8 speaker extra and return extra wire | Rmt. |  | 1 | 15 |  |  | 15
| Total qty. | [6 empty] | 64.1
| previous qty | [6 empty] | 64.1
| this bill qty. | [6 empty] | 0
10 | Supply of 3x1.5 Sq.mm FRLS Microphone Cable The cost of conduit shall be paid separately. | Mtr. | RO
11 | Supply of 12U (600mmx800mm) Equipment Rack | Nos. | 1
12 | Supply & Laying of 25mm dia. GI Conduit | Mtr. | 50
| DB to Ceiling level | Rmt. |  | 1 | 3 |  |  | 3
| Ceiling to rafter | Rmt. |  | 1 | 4.2 |  |  | 4.2
| Ceiling to rafter down | Rmt. |  | 1 | 1.6 |  |  | 1.6
| Long rafter | Rmt. |  | 1 | 9.2 |  |  | 9.2
| Rafter to center rafter | Rmt. |  | 1 | 3 |  |  | 3
| Center rafter | Rmt. |  | 1 | 7.2 |  |  | 7.2
| Center rafter return | Rmt. |  | 1 | 7.2 |  |  | 7.2
| center rafter to corner rafter | Rmt. |  | 1 | 3 |  |  | 3
| Long rafter 2nd | Rmt. |  | 1 | 9.2 |  |  | 9.2
| Total qty. | [6 empty] | 47.6
| previous qty | [6 empty] | 47.6
| this bill qty. | [6 empty] | 0
TOTAL FOR MUSIC SYSTEM EQUIPMENTS