## MEP
PROJECT : AMD, CIP LOUNGE AT T1, AHEMDABAD AIRPORT
Date | October' 27, 2023
S.NO | ITEM DESCRIPTION | UNIT | QTY. | Rate (INR) | Amount (INR)
Part I | Electrical
A | SUB HEAD I - WIRING
1.1 | Wiring for primary light points for Switch controlled points with 2.5 sq. mm LSHF PVC insulated stranded /multi stranded copper conductor 1100 Volt grade wires in IS embossed 25mm dia 16 SWG GI surface /concealed conduit including cost of providing saddles hangers supports from soffit of slab etc for surface conduiting, ceiling conduiting and/or cost of cutting and filling chases for recessed conduiting, and including the cost of Supply and fixing a 6 amp 240 Volt grid plate mounted switch with moulded cover plate in zinc chromate passivated GI box and including the cost of running 1.5 sq. mm LSHF PVC insulated copper earth wire for loop earthing etc. complete as directions of Engineer-in-charge and as required. | nos | 18 | 1355 | 24390
1.2 | Wiring for secondary light points with 1.5 sq. mm LSHF PVC insulated stranded/multistranded copper conductor 1100 Volt grade wires in surface/concealed in IS embossed 25mm dia 16 SWG GI conduit including cost of providing saddles hangers supports from soffit of slab etc for surface conduiting, ceiling conduiting and/or cost of cutting and filling chases for recessed conduiting including the cost of running 1.5 sq. mm LSHF PVC insulated copper earth wire for loop earthing etc. complete as directions of Engineer-in-charge and as required. (Normal) | nos | 24 | 1146 | 27504
1.3 | Wiring for secondary light points with 1.5 sq. mm LSHF PVC insulated stranded/multistranded copper conductor 1100 Volt grade wires in surface/concealed in IS embossed 25mm dia 16 SWG GI conduit including cost of providing saddles hangers supports from soffit of slab etc for surface conduiting, ceiling conduiting and/or cost of cutting and filling chases for recessed conduiting including the cost of running 1.5 sq. mm LSHF PVC insulated copper earth wire for loop earthing etc. complete as directions of Engineer-in-charge and as required. (Emergency) | nos | 5 | 1146 | 5730
1.4 | Wiring for primary light points for DB / Dimmer/ Sensor/ Automation controlled points with 2.5 sq mm LSHF PVC insulated stranded/multi stranded copper conductor 1100 Volt grade wires in IS embossed 25mm dia 16 SWG GI surface/concealed conduit including cost of providing saddles etc for surface conduiting and/or cost of cutting and filling chases for recessed conduiting and including the cost of running 1.5 sq mm LSHF PVC insulated copper earth wire for loop earthing etc. complete as directions of Engineer-in-charge and as required. (Cost of MCB/Switch shall be consider in this item).(Normal) | nos | 68 | 1345 | 91460
1.5 | Wiring for secondary light points with 1.5 sq. mm LSHF PVC insulated stranded/multistranded copper conductor 1100 Volt grade wires in surface/concealed in IS embossed 25mm dia 16 SWG GI conduit including cost of providing saddles hangers supports from soffit of slab etc for surface conduiting, ceiling conduiting and/or cost of cutting and filling chases for recessed conduiting including the cost of running 1.5 sq. mm LSHF PVC insulated copper earth wire for loop earthing etc. complete as directions of Engineer-in-charge and as required. (Normal) | nos | 251 | 1050 | 263550
1.6 | Wiring for primary light points for DB/ Dimmer/ Sensor/ Automation controlled points with 2.5 sq mm LSHF PVC insulated stranded/multi stranded copper conductor 1100 Volt grade wires in IS embossed 25mm dia 16 SWG GI surface/concealed conduit including cost of providing saddles etc for surface conduiting and/or cost of cutting and filling chases for recessed conduiting and including the cost of running 1.5 sq mm LSHF PVC insulated copper earth wire for loop earthing etc. complete as directions of Engineer-in-charge and as required. (Cost of MCB/Switch shall be consider in this item). (Emergency) | nos | 11 | 1345 | 14795
1.7 | Wiring for secondary light points with 1.5 sq. mm LSHF PVC insulated stranded/multistranded copper conductor 1100 Volt grade wires in surface/concealed in IS embossed 25mm dia 16 SWG GI conduit including cost of providing saddles hangers supports from soffit of slab etc for surface conduiting, ceiling conduiting and/or cost of cutting and filling chases for recessed conduiting including the cost of running 1.5 sq. mm LSHF PVC insulated copper earth wire for loop earthing etc. complete as directions of Engineer-in-charge and as required. (Emergency) | nos | 39 | 1050 | 40950
1.8 | Wiring for 240 volt 6 amp Multistandard single phase and neutral switch socket outlet with 4 sq. mm LSHF PVC insulated stranded/multi stranded copper conductor 1100 Volt grade wires in IS embossed 25mm dia 16 SWG GI surface/concealed conduit including cost of providing circuit wiring with 4 sq mm LSHF PVC insulated stranded/ multistranded copper conductor 1100 volt grade wires and including the cost of providing saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and Supply and fixing of a 240 volt 6 amp Multistandard socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed zinc chromate passivated GI box and including earthing of the 3rd pin with 2.5 sq. mm LSHF PVC insulated copper earth wire conductor wires complete as directions of Engineer-in-charge and as required. | nos | 6 | 780 | 4680
1.9 | Wiring as in Item 1.8 above looped from an adjacent switch socket outlet as required and Supply and fixing of a combined 240 volt 6 amp Multistandard socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed zinc chromate passivated GI box and including earthing of the 3rd pin with 2.5 sq. mm LSHF PVC insulated copper earth wire conductor wires complete as directions of Engineer-in-charge and as required. | nos | 23 | 1225 | 28175
1.1 | Wiring for a 240 volt 6-16 amp single phase and neutral universal switch socket outlet with 6.0 sq. mm LSHF PVC insulated stranded copper conductor 1100 Volt grade wires in 25 mm dia GI surface/concealed conduit including the cost of providing circuit wiring with 4.0 sq mm LSHF PVC insulated stranded copper conductor 1100 volt grade wires and including cost of providing brackets, saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and providing and fixing of a combined multi-pin 240 volt 6-16 amp universal socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed galvanized box and including earthing of the 3rd pin with 4.0 sq mm 1100 volt grade LSHF PVC insulated stranded copper conductor wires complete as directions of Engineer-in-charge and as required. | nos | 30 | 880 | 26400
1.11 | Wiring as in Item 1.10 above looped from an adjacent switch socket outlet as per specifications and directions of Engineer-in-charge and providing and fixing of a modular type multi-pin 240 Volt 6-16 amp shuttered socket outlet and a modular type 16 amp 240 Volt single pole rocker type switch in a recessed galvanized boxes with internal wiring and moulded front plates complete as directions of Engineer-in-charge and as required. | nos | 20 | 1225 | 24500
1.12 | Wiring for a 240 volt 16 amp single phase and neutral universal switch socket outlet with 4.0 sq. mm LSHF PVC insulated stranded copper conductor 1100 Volt grade wires in 25 mm dia GI surface/concealed conduit including the cost of providing circuit wiring with 4.0 sq mm LSHF PVC insulated stranded copper conductor 1100 volt grade wires and including cost of providing brackets, saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and providing and fixing of a combined multi-pin 240 volt 6-16 amp universal socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed galvanized box and including earthing of the 3rd pin with 4.0 sq mm 1100 volt grade LSHF PVC insulated stranded copper conductor wires complete as directions of Engineer-in-charge and as required. | nos | 22 | 1140 | 25080
1.13 | Wiring as in Item 1.12 above looped from an adjacent switch socket outlet as per specifications and directions of Engineer-in-charge and providing and fixing of a modular type multi-pin 240 Volt 16 amp shuttered socket outlet and a modular type 16 amp 240 Volt single pole rocker type switch in a recessed galvanized boxes with internal wiring and moulded front plates complete as directions of Engineer-in-charge and as required. | nos | 12 | 1185 | 14220
1.14 | Supply , Installation, Testing and comissioning of IP 66 EGA Boxes with all standard accessories consisting of following: a) 3nos 6-16 amp socket with single Switch b) 2nos Data outlets with includes of Data wiring and terminations. Wiring for socket outlet with 4.0 sq. mm LSHF PVC insulated stranded copper conductor 1100 Volt grade wires in 25 mm dia GI surface/concealed Conduit / Raceways including the cost of providing circuit wiring with 4.0 sq mm LSHF PVC insulated stranded copper conductor 1100 volt grade wires and including cost of providing brackets, saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and providing and fixing of a EGA Box complete as directions of Engineer-in-charge and as required. | nos | RO | 1310 | -
1.15 | Supply , Installation, Testing and comissioning of IP66 Overdesktop pop up Boxes with all standard accessories consisting of following: a) 3nos 6-16 amp socket with two Number Switches b) 2nos Data outlets with includes of Data wiring and terminations. Wiring for socket outlet with 4.0 sq. mm LSHF PVC insulated stranded copper conductor 1100 Volt grade wires in 25 mm dia GI surface/concealed Conduit / Raceways including the cost of providing circuit wiring with 4.0 sq mm LSHF PVC insulated stranded copper conductor 1100 volt grade wires and including cost of providing brackets, saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and providing and fixing of a Overdesktop Flip Box complete as directions of Engineer-in-charge and as required. | nos | 4 | 4215 | 16860
1.16 | Supply , Installation, Testing and comissioning of Pop up Boxes/IP 66 floor EGA box on furnitre/wall with all standard accessories consisting of following: a) 2 nos 6-16 amp socket with single Switch b) 1 nos Data outlets with includes of Data wiring and terminations. Wiring for socket outlet with 4.0 sq. mm LSHF PVC insulated stranded copper conductor 1100 Volt grade wires in 25 mm dia GI surface/concealed Conduit / Raceways including the cost of providing circuit wiring with 4.0 sq mm LSHF PVC insulated stranded copper conductor 1100 volt grade wires and including cost of providing brackets, saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and providing and fixing of a Floor EGA Box/furniture/wall pop up up box complete as directions of Engineer-in-charge and as required. | nos | 40 | 1695 | 67800
1.17 | Supply , Installation, Testing and comissioning of wall/furniture pop up Boxes with all standard accessories consisting of following: a) 1nos 6-16 amp socket with single Switch b) 1nos Data outlet with includes of Data wiring and terminations. Wiring for socket outlet with 4.0 sq. mm LSHF PVC insulated stranded copper conductor 1100 Volt grade wires in 25 mm dia GI surface/concealed Conduit / Raceways including the cost of providing circuit wiring with 4.0 sq mm LSHF PVC insulated stranded copper conductor 1100 volt grade wires and including cost of providing brackets, saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and providing and fixing of the Box outlets complete as directions of Engineer-in-charge and as required. | nos | 6 | 1775 | 10650
1.18 | Providing and fixing of 2nos. Data outlet plate mounted outlet unit (RJ-45) with moulded cover plate in recessed zinc chromate passivated MS box complete as directions of Engineer-in-charge and as required for Data system. (For Display) | nos | 10 | 610 | 6100
1.19 | Providing and fixing of 1no. Data outlet plate mounted outlet unit (RJ-45) with moulded cover plate in recessed zinc chromate passivated MS box complete as directions of Engineer-in-charge and as required for Data system. | nos | 10 | 465 | 4650
1.2 | Supplying, laying, testing and commissioning of 4-pair Non-plenum Enhanced Cat 6 unshielded twisted pair computer cable with 24 AWG solid copper conductors in surface/concealed conduit/raceways/modular furniture , complete as directions of Engineer-in-charge and as required. | Mtrs | 1540 | 186 | 286440
1.21 | Supplying, Installation, testing and commissioning of 12U Networking Rack with network switches, including I/o's, patch cords, connectors/ends, PDUs etc. and all accessories including and complete as required | nos | 1 | 43000 | 43000
1.22 | Supplying, Installation, testing and commissioning of Occupancy Sensor for light control with all accessories and complete as directions of Engineer-in-charge and as required. | nos | 10 | 2087 | 20870
1.23 | Wiring for 25 amp SPN isolator in weatherproof enclosure with 6.0 sq. mm LSZH PVC insulated standed/multi stranded copper conductor 1100 volt grade wires in FRLSH PVC surface/concealed conduit including cost of providing saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and including providing and fixing of a 25 amp terminal block in recessed GI box with conduit Bend out for connection to equipment including earthing with 2 nos 4.0 sq mm 1100 volt grade PVC insulated FRLS multistranded copper conductor wire complete as directions of Engineer-in-charge and as required. | Nos. | RO | 3185
1.24 | Supplying and drawing wiring with single core stranded copper conductor PVC insulated 1100 volt grade LSHF PVC insulated wires in IS embossed suitable dia 16/14 SWG GI surface/concealed conduit including cost of providing saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required including the cost of running copper conductor LSHF PVC insulated loop earthing wire complete as directions of Engineer-in-charge and as required as below.
a) | 2 x 1.5 sq mm with 1 x 1.5 sq mm earth wire | Mtrs | RO | 185
b) | 2 x 2.5 sq mm with 1 x 2.5 sq mm earth wire | Mtrs | 50 | 186 | 9300
c) | 2 x 4 sq mm with 1 x 4.0 sq mm earth wire | Mtrs | 100 | 235 | 23500
d) | 2 x 6 sq mm with 1 x 6.0 sq mm earth wire | Mtrs | 500 | 290 | 145000
e) | 2 x 10 sq mm with 1 x 10 sq mm earth wire | Mtrs | RO | 395
f) | 4 x 2.5 sq mm with 2 x 2.5 sq mm earth wire | Mtrs | RO | 390
g) | 4 x 4 sq mm with 2 x 4.0 sq mm earth wire | Mtrs | RO | 450
h) | 4 x 6 sq mm with 2 x 6.0 sq mm earth wire | Mtrs | 70 | 565 | 39550
i) | 4 x 10 sq mm with 2 x 10 sq mm earth wire | Mtrs | RO | 1150
j) | 4 x 16 sq mm with 2 x 16 sq mm earth wire | Mtrs | RO | 1860
1.25 | Supplying and drawing recessed/surface IS embossed GI conduiting system including cost of providing saddles etc for recessed and/or surface, in floor conduiting and/or cost of cutting and filling chases for recessed conduiting and painting complete as directions of Engineer-in-charge and as required as below.
a) | 25 mm 16 SWG | Mtrs | 250 | 186 | 46500
b) | 32 mm 14 SWG | Mtrs | 300 | 240 | 72000
c) | 40 mm 14 SWG | Mtrs | 190 | 290 | 55100
d) | 50 mm 14 SWG | Mtrs | 50 | 353 | 17650
1.26 | Supply and fixing GI flexible conduit including all fittings complete as required as below.
a) | 20 mm 16 SWG | Mtrs | 50 | 162 | 8100
b) | 25 mm 16 SWG | Mtrs | 130 | 186 | 24180
c) | 32 mm 14 SWG | Mtrs | 50 | 240 | 12000
d) | 40 mm 14 SWG | Mtrs | 40 | 290 | 11600
e) | 50 mm 14 SWG | Mtrs | RO | 375
1.27 | Supplying and fixing heavy gauge ISI embossed PVC recessed and/or surface conduits including cost of providing saddles etc for surface conduiting and/or cost of cutting and filling chases for recessed conduiting complete as per specifications, as required and as below.
a) | 25 mm 16 SWG | Mtrs | 250 | 58.5 | 14625
b) | 32 mm 14 SWG | Mtrs | 50 | 88 | 4400
c) | 40 mm 14 SWG | Mtrs | 5 | 118 | 590
| TOTAL SUB-HEAD I carried over to Summary |  |  |  | 1531899
B | SUB HEAD-II- CABLES & RACEWAYS
1 | Supply and laying cables on Tray / clamped to wall with suitable clamps saddles and fixing bolts/ in ground including the cost of digging and back filling with sand and brick protection as required and including testing and commissioning of the following 1100 volt grade armoured XLPE insulated and PVC sheathed copper conductor cable complete as required with single core flexible cupper wire for Earhting .The costs shall include for all cables to be provided with a 1D gap and shall be properly clamped with cable clamps and ties. Identification tags shall be provided for all cables and route markers for cables in ground.
a) | 4C x 35 sqmm + 2Rx1CX16sqmm | Mtrs | RO | 550
b) | 4C x 25 sqmm + 2Rx1CX25sqmm | Mtrs | RO | 420
c) | 4C x 10 sqmm + 2Rx1CX10sqmm | Mtrs | RO | 1175
d) | 4C x 6 sqmm + 2Rx1XCX6sqmm | Mtrs | RO | 750
e) | 4C x 4 sqmm + 2Rx1CX4sqmm | Mtrs | RO | 685
2 | Supply and laying cables on Tray / clamped to wall with suitable clamps saddles and fixing bolts/ in ground including the cost of digging and back filling with sand and brick protection as required and including testing and commissioning of the following 1100 volt grade armoured XLPE insulated and PVC sheathed Aluminium conductor cable complete as required. The costs shall include for all cables to be provided with a 1D gap and shall be properly clamped with cable clamps and ties. Identification tags shall be provided for all cables and route markers for cables in ground.
a) | 4C x 120 sqmm + 2RX25X3 GI Strip for Earthing | Mtrs | RO | 3800
3 | Cable end termination of the following XLPE insulated and PVC sheathed copper conductor cable 1100 Volt grade including cost of crimping heavy duty copper lugs,nickel plated brass double compression glands,insulation tape and all requisite material for completion of termination complete as required and as below.
a) | 4C x 120 sqmm | Nos | RO | 4000
b) | 4C x 35 sqmm + 2Rx1CX16sqmm | Nos | RO | 4485
c) | 4C x 25 sqmm + 2Rx1CX25sqmm | Nos | RO | 3800
d) | 4C x 10 sqmm + 2Rx1CX10sqmm | Nos | RO | 3500
e) | 4C x 6 sqmm + 2Rx1XCX6sqmm | Nos | RO | 1200
f) | 4C x 4 sqmm + 2Rx1CX4sqmm | Nos | RO | 1050
4 | Supply, laying cables on Tray / clamped to wall with suitable clamps saddles and fixing bolts as required and including testing and commissioning of the following 1100 volt grade armoured XLPE insulated and PVC sheathed copper/Aluminium conductor cable complete as required with single core flexible copper wire for Earhting .The costs shall include for all cables to be provided with a 1D gap and shall be properly clamped with cable clamps and ties. Identification tags shall be provided for all cables and route markers for cables in ground.
a) | 3.5C x 240 sqmm AL. AR. XLPE Cable (From existing Nearby Terminal Electrical Panel) | Mtrs | RO | 4485
b) | 3.5C x 150 sqmm AL. AR. XLPE Cable | Mtrs | RO | 3770
c) | 3.5C x 95 sqmm AL. AR. XLPE Cable | Mtrs | RO | 3520
d) | 4C x 35 sqmm AL. AR. XLPE Cable | Mtrs | RO | 4500
e) | 4C x 25 sqmm AL. AR. XLPE Cable | Mtrs | RO | 4200
f) | 4C x 16 sqmm CU. AR. XLPE Cable | Mtrs | 40 | 1150 | 46000
g) | 4C x 10 sqmm CU. AR. XLPE Cable | Mtrs | 20 | 1087 | 21740
h) | 4C x 6 sqmm CU. AR. XLPE Cable | Mtrs | 160 | 795 | 127200
i) | 4C x 4 sqmm CU. AR. XLPE Cable | Mtrs | 50 | 730 | 36500
j) | 3C x 10 sqmm CU. AR. XLPE Cable | Mtrs | 25 | 3540 | 88500
5 | Supply and laying cables on Tray / clamped to wall with suitable clamps saddles and fixing bolts/ in ground including the cost of digging and back filling with sand and brick protection as required and including testing and commissioning of the following 1100 volt grade armoured XLPE insulated and PVC sheathed Aluminium conductor cable complete as required. The costs shall include for all cables to be provided with a 1D gap and shall be properly clamped with cable clamps and ties. Identification tags shall be provided for all cables and route markers for cables in ground.
a) | 4C x 120 sqmm + 2RX25X3 GI Strip for Earthing | Mtrs | RO | 3800
6 | Cable end termination of the following XLPE insulated and PVC sheathed aluminium conductor cable 1100 Volt grade including cost of crimping heavy duty aluminium lugs, nickel plated brass compression glands, insulation tape and all requisite material for completion of termination complete as required and as below, including tagging oif each.
a) | 3.5C x 240 sqmm AL. AR. XLPE Cable | Nos. | RO | 4485
b) | 3.5C x 150 sqmm AL. AR. XLPE Cable | Nos. | RO | 3770
c) | 3.5C x 95 sqmm AL. AR. XLPE Cable | Nos. | RO | 3520
d) | 4C x 35 sqmm AL. AR. XLPE Cable | Nos. | RO | 4500
e) | 4C x 25 sqmm AL. AR. XLPE Cable | Nos. | RO | 4200
7 | Cable end termination of the following XLPE insulated and PVC sheathed copper conductor cable 1100 Volt grade including cost of crimping heavy duty copper lugs, nickel plated brass compression glands,insulation tape and all requisite material for completion of termination complete as required and as below, including tagging oif each.
a) | 4C x 16 sqmm CU. AR. XLPE Cable | Nos. | 4 | 1175 | 4700
b) | 4C x 10 sqmm CU. AR. XLPE Cable | Nos. | 2 | 1110 | 2220
c) | 4C x 6 sqmm CU. AR. XLPE Cable | Nos. | 8 | 810 | 6480
d) | 4C x 4 sqmm CU. AR. XLPE Cable | Nos. | 4 | 740 | 2960
e) | 3C x 10 sqmm CU. AR. XLPE Cable | Nos. | 2 | 3610 | 7220
8 | Supply and fixing of perforated sheet steel slotted cable trays with vertical sides on both ends as per approved design and GI angle supports spaced 1000 mm apart throughout the length as specified, including the cost of 1 meter GI rod hangers, hooks, dash fasteners, painting etc. for suspension from ceiling complete as required.
a) | 300 mm width x 50 mm depth x 1.6 mm thickness | Mtrs | 35 | 1260 | 44100
b) | 150 mm width x 50 mm depth x 1.6 mm thickness | Mtrs | 30 | 1305 | 39150
c) | 100 mm width x 50 mm depth x 1.6 mm thickness | Mtrs | 80 | 1117 | 89360
GI Raceway & Junction boxes (IP 55)
9 | Supply, assembly and laying of under floor trunking (comparmentalized) made out of minimum 1.6mm thick pre galavised sheet with enamel paint finish complete with jointing sleeve, horizontal bends, vertical bends, level adjustment components and closer, vertical elbow, covers, access outlet. etc. complete with all other accessories under floor installation including cutting and chasing the floor/ or on surface, making good the same, placing in position and cleaning from inside complete etc. as required. All sizes shall be with 2mm thick covers.
a) | 300 mm x 40 mm (3 compartment - 1 For Power, 1 for Data) | Mtrs | 35 | 1490 | 52150
a) | 150 mm x 40 mm (2 compartment - 1 For Power, 1 for Data) | Mtrs | 30 | 1396 | 41880
b) | 100 mm x 40 mm (2 compartment - 1 For Power, 1 for Data) | Mtrs | 120 | 1352 | 162240
c) | 75 mm x 40 mm (1 compartment) | Mtrs | 10 | 1210 | 12100
d) | Providing and fixing 350 x 350 x 50 mm deep junction box | Nos | 15 | 1538 | 23070
e) | Providing and fixing 200 x 200 x 50 mm deep junction box | Nos | 4 | 1117 | 4468
f) | Providing and fixing 150 x 150 x 50 mm deep junction box | Nos | 20 | 795 | 15900
| TOTAL SUB-HEAD II carried over to Summary |  |  |  | 827938
C | SUB HEAD III - DISTRIBUTION SYSTEM & ELECTRICAL PANEL
1 | Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof distribution boards constructed from 1.2mm sheet steel IP 42 construction,double door finished with rust proof red oxide coating and two coats of paint with hinged gasketted door and housing the following complete with suitably rated PVC insulated copper busbars with interconnections and neutral bar assembly, earthing terminals complete as approved by Architects. Padlocking facility shall be provided on the door.
a) | 4 WAY TPN | nos | RO | 22500
32 amp TPN 10 kA MCB with thermal magnetic protective releases incoming with 3 single phase banks each comprising of 1-32 amp DP 30 mA RCCB incoming and 12 nos 6/16/20/25/32 amps SP 10 kA MCB with thermal magnetic protective releases out goings.
b) | 8 WAY TPN | nos | RO | 31500
1-32 amp TPN 10 kA MCB with thermal magnetic protective releases incoming with 3 single phase banks each comprising of 1-100 amp DP 30 mA RCCB incoming and 24 nos 6/16/20/25/32 amps SP 10 kA MCB with thermal magnetic protective releases out goings.
c) | 12 WAY TPN | nos | 2 | 31188 | 62376
1-63 amp FP 10 kA MCB with incoming with 3 single phase banks each comprising of 1-63 amp DP 100 mA RCCB incoming and 36 nos 25/32 amps SP 10 kA MCB with thermal magnetic protective releases out goings.
d) | 12 WAY TPN | nos | 3 | 29325 | 87975
1-40 amp TPN 10 kA MCB with incoming with 3 single phase banks each comprising of 1-40 amp DP 30 mA RCCB incoming and 36 nos 10/16 amps SP 10 kA MCB with thermal magnetic protective releases out goings.
e) | Supply and fixing of 25 amps , 230 volt , 10 KA DP isolators in weatherproof enclosure with all the neccessry assosiaries (IP 66) for Airwasher & Scrubber at roof | nos | RO | 3500
f) | Supply and fixing of 1 no. 6/16 amps switch socket in weatherproof enclosure with all the neccessry assosiaries (IP 66) for Inline fans at roof | nos | 7 | 3910 | 27370
g) | Supply and fixing of 1 no. 32 amps TPN industrial socket with 32A MCB in weatherproof enclosure with all the neccessry assosiaries | nos | RO | 4200
h) | Supply and fixing of 1 no. 32 amps 5 Pole industrial socket with 32A MCB in weatherproof enclosure with all the neccessry assosiaries | nos | 1 | 6175 | 6175
i) | Supply and fixing of 1 no. 32 amps SPN industrial socket with 32A MCB in weatherproof enclosure with all the neccessry assosiaries | nos | 10 | 4655 | 46550
2 | Design, Manufacture, Supply, delivery and coordination for Installation of the following front operated modular compartmentalised construction cubicle type, front access, dead back, 2mm thick steel enclosed free standing / wall mounted, dust and vermin proof, switchboard with IP42/ Specified protection with hinged and lockable doors duly powder coated complete with interconnections, tinned copper crimping lugs, bonding to earth and painting, suitable for use at 415 volts, 3 phase 4 wire 50 Hz system, and to withstand a symetrical fault level of 25 kA
Switchboard shall have provision for entry of cables from the top or bottom as required.
All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The Busbars insulation shall be with heat shrinkable sleeves. SMC/DMC shrouds and busbar supports shall be used. Padlocking facility shall be provided on all outgoing feeders doors and switch handles shall be lockable in OFF position
All kA values indicated shall be Ics breaking capacity.
The cost shall include providing and fixing of 75 x 50 x 6 mm channels for switchboard support.
All MCCB shall have rotary handles & extension terminal, phase barrier on both sides as required at site.
GA drawings shall be got approved from Owners/ Architects/ Consultants before fabrication.
All outgoing MCCBs with thermal magnetic based adjustable release MCCB with front operating handle for O/C, S/C & earth fault protection of following capacity and rating, 16 KA (Ics=Icu upto 433 V ) with front operating handle, Spreader links and phase barrier, solid neutral link complete with wiring, connections etc.
Note:- The Manufacturer/Supplier shall supervise the installation, testing and commissioning of the cubicle panels by the electrical contractor/Engineer-in-charge
Electrical Panel
A | INCOMING
1 no 160 A , 25 KA 4P MCCB thermal magnetic type
B | INDICATING PANEL
The incomers shall have the following indicating panel
a) | 3 nos Cast resin current transformers of 150/5 ratio Class 1.0 for metering
b) | 1 no Multi function meter (BMS & SCADA Compitable)
c) | 1 set of three phase indicating lamps (R,Y,B)
d) | ON, OFF, Trip indicating lamps (LED type)
e) | 2A , SP MCB 10KA for metering and monitoring circuit.
C | BUSBAR
a) | Electrolytic high conductivity aluminium three phase and neutral busbars rated at 160 amps suitable to with stand symmetrical fault level of 25kA at 415 volts. The neutral busbar is to be of 100% capacity.
b) | 1 set of three phase indicating lamps (R,Y,B)
D | OUTGOING UNITS
a) | 2 nos 100A 4P 25 kA MCB with thermal magnetic protective release
b) | 3 nos 40A 4P 25 kA MCB with thermal magnetic protective release
c) | 5 nos 32A 4P 25 kA MCB with thermal magnetic protective release
| The Switchboard shall be complete with all interconnections, risers, internal wiring, labels etc complete as required | nos | RO | 350000
UPS 15 kVA
3 | Supply, installation, testing and commissioning of 15 kVA UPS system comprising of online units with a battery backup of 30 minutes duration for full load and with all standards fittings, accessories, protection, instruments, indications and controls including but not restricted to transformer, rectifier, inverter, SMF battery with float cum boost battery charger, static bypass switch, maintenance bypass, interconnections etc. The UPS shall be suitble for three phase 415V output with variation of + 15% and give constant output supply of 415V + 2%. The UPS shall have 2 earthing connection with two seperate earth pits. | nos | 1 | 370880.2 | 370880.2
4 | Supply, installation, testing & commissioning of MAINTENANCE FREE earthing system with Earthing Electrode dual pipe consist of 3mtr long 77 mm dia outer pipe, 47 mm dia inner pipe, Terminal flat of 38 x 10 mm, the entire construction processed with Hot Dip Galvanization, outer surface upto 100 microns and all inner surface Upto 300 microns, all inner annular space filled with highly conductive and non-corrosive nature crystalline material, along with electrode Moisture Booster compound of 2 x 25 kg bags to fill surround the pipe at the time of installation. (Moisture Booster having its property of moisture retention, conduction and non – corrosive nature) .Also include 300mm x 300mm heavy duty GI frame and heavy duty RCC Pre cast cover, 150mm brick masonry chamber etc. for UPS earthing | nos | RO
a | 2R X 1C X 6sqmm Copper Cable | mtr | RO
b | 40 Amp 4 pole isolator (25KA) | nos | RO
5 | Supplying and laying of the following earthing strip on cable tray/ wall clamped to wall with suitable clamps saddles and fixing bolts/soldering /riveting in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043:1987. All joints shall be timed.
a) | 32 mm x 6 mm GI strip | Mtrs | 40 | 630 | 25200
b) | 25 mm x 3 mm GI strip | Mtrs | 260 | 436 | 113360
b) | 25 mm x 3 mm Copper strip | Mtrs | 50 | 515 | 25750
c) | 6 SWG GI Wire | Mtrs | 210 | 1117 | 234570
d) | 8 SWG GI Wire | Mtrs | 50 | 1275 | 63750
e) | 4 Sqmm bare, tinned-copper stranded conductor | Mtrs | 100 | 441 | 44100
6 | Supply and fixing of 1.1 KV grade rubber mat 914.4 mm wide 6mm thick to withstand 1.1 KV dielectric strength in front of each panel. | nos | 1 | 9025 | 9025
| TOTAL SUB-HEAD III carried over to Summary |  |  |  | 1117081.2
F | SUB HEAD VI - INSTALLATION OF LIGHT FIXTURES
NOTE : a) Any of fixtures and fittings shall be re-confirmed with the Architects/ consultants before ordering/installing them. b) All light Fixtures should be approved by consultant / architect/client from the given make list before installations. c) All the marking & cutting of light fixtures should be in electrical contractor's scope.
1 | Installation, testing and commissioning (including fixing flexible wires from holder/junction box to fixtures hardwares and its driver's wiring, installation etc.) of following light fixtures:
1.1 | 5W Floor light fixture | NOS. | 30 | 245 | 7350
1.2 | 6W Table lamp | NOS. | 30 | 245 | 7350
1.3 | 15W Table lamp | NOS. | 3 | 980 | 2940
1.4 | 7W Ceiling light fixture | NOS. | 32 | 245 | 7840
1.5 | 9W Circular ceiling light fixture | NOS. | 89 | 245 | 21805
1.6 | 9W Vertical led cove light- reception wall arch. | NOS. | 22 | 245 | 5390
1.7 | 9W Square ceiling light fixture | NOS. | 26 | 245 | 6370
1.8 | 30W 2x2 light fixture | NOS. | 4 | 785 | 3140
1.9 | Cove light | RM | 410 | 145 | 59450
2 | Pendant light fixture (semi circle) | NOS. | 8 | 1960 | 15680
2.1 | 25 leaf shape flower pattern feature light | NOS. | 30 | 8330 | 249900
2.2 | 12 leaf shape flower pattern feature light fixture | RM | 385 | 785 | 302225
2.3 | Chandelier light-1 (p6) | NOS. | 12 | 6860 | 82320
2.4 | 10W Mirror light | NOS. | 5 | 1175 | 5875
2.5 | Reception chandelier light | NOS. | 1 | 10300 | 10300
2.6 | Island counter chandelier light(double oval shape) | NOS. | 2 | 3430 | 6860
2.7 | Semi arch shape pendant light - corridor | NOS. | 4 | 1470 | 5880
2.8 | Semi arch shape pendant light - corridor | NOS. | 3 | 1470 | 4410
2.9 | Chandelier light-2 (p2)-book shelf area-quit zone | NOS. | 3 | 8330 | 24990
| TOTAL SUB-HEAD VI carried over to Summary |  |  |  | 830075

## LOM-MEP
PROJECT : AMD, CIP LOUNGE AT T1, AHEMDABAD AIRPORT
S. No | Equipment/Item/Material | Approved Makes
LIST OF MAKES ELECTRICAL
1 | MCBs /MCCB/ELCBs | LEGRAND/L&T/SCHNEIDER/ABB/SIEMENS / C&S
2 | CABLE TRAYS & RACEWAY ACCESSORIES | SUPERMAX / INDIANA / PELCO / SLOTCO
3 | CABLE TRAY STEEL SUPPORTS | SUPERMAX / INDIANA / PELCO / SLOTCO
4 | GI PIPES | JINDAL (HISSAR)/TATA (ISI)
5 | HDPE (DWC) PIPES | DURALINE/ REX/ TIRUPATI
6 | MCB DISTRIBUTION BOARDS | SCHNEIDER/LEGRAND/SIEMENS/L & T
7 | L.T. CABLES & CONTROL CABLES | POLYCAB /HAVELLS / NATIONAL / ICC / KEI/SKYTONE/ GEMSCAB/ BONTON
8 | CABLE GLAND | COMMET/HMI/GRIPWELL
9 | LUG/ TERMINAL BLOCKS | DOWELL’S/REYCHAM/COMMET/ WAGO/ ELMEC
10 | BATTERIES | EXIDE/HBL/ROCKET/STANDARD/AMCO/CUMMINS
11 | UPS | APC/EMERSON/ABB/ GUTOR
12 | WIRE | FINOLEX/ HAVELLS/ POLYCAB/ KEI
13 | RACEWAYS | MK/LEGRAND/ SCHNEIDER
14 | PLOYCARBONATE JUNCTION BOX | SINTEX/MK/LEGRAND
15 | GI CONDUIT | BEC/AKG/ NIC/STEEL CRAFT/JINDAL
16 | GI CONDUIT ACCESSORIES | RAMA/ SHARMA SALES CORPORATION / FIT WELL/ AKG
17 | MODULAR PLATE TYPE SWITHCH / SOCKET GI BOXES / FAN REGULATOR/TELEPHONE SOCKET | MK (WRAPAROUND)/ LEGRAND (MYRIUS)/ SCHNEIDER (ZENCELO) / NORTH WEST (STYLUS) / CRABTREE (ATHENA)
18 | TELEPHONE CABLES / WIRES / CO-AXIAL TV CABLES | FINOLEX/POLYCAB/ HAVELLS/ RR KABLE/ SKYDA/ BCH/ L&T/ DALTON
19 | CAT 6 CABLE / CAT 6A / FIBER OPTIC CABLE & ASSOCIATED ITEMS | SCHNEIDER/ SIEMON/ SYSTIMAX
20 | TELEPHONE TAG BLOCK | KRONE (GERMAN) /POUYET
21 | LUGS / FERRULES / THIMBLES | DOWELLS / JAINSON
22 | OCCUPANCY SENSOR | PHILIPS /WIPRO /GE
23 | RJ-45 MODULAR SOCKET WITH PLATE | AMP/ SCHEINDER/ SIEMON / SYSTIMAX
24 | DATA RACK & ACCESSORIES | SCHNEIDER, RITTAL, VALRACK
25 | MAIN FIRE ALARM CONTROL PANEL | NOTIFIER/HONEYWELL/ EDWARD/SIEMENS/BOSCH
26 | MULTI CRITERIA/SMOKE DETECTOR | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
27 | INTELLIGENT HEAT | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
28 | SPEAKERS | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
29 | DIGITAL VOICE EVACUATION SYSTEM | NOTIFIER/HONEYWELL/GAMEWELL/SIEMENS/BOSCH
30 | CCTV | CP PLUS/HIKVISION/ZICOM/PELCO
31 | EMERGENCY CALL SYSTEM | ZENTAL- NORWAY, SIEMENS, HONEYWELL
32 | DISTRIBUTION PANEL | NEPTUNE/ABB/ADLEC/ADVANCE
33 | FAULT ISOLATOR | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
34 | RESPONSE INDICATOR | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
35 | CONTROL MODULE | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
36 | HOOTER | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
37 | MANUAL CALL POINT | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
38 | MICROPHONE | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
39 | MICROPHONE WITH TABLE | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
LIST OF MAKES HVAC
1 | AIR HANDLING UNIT | VTS/EDGETECH/CARYAIRE/WAVES
2 | AIR WASHER/SCRUBBER | EDGETECH/ZECO/WAVES
3 | INLINE FAN | KRUGER/ SYSTEM AIR/ GREENHECK
4 | FACTORY/SITE FABRICATED DUCT | ZECO/ DUCTOFAB/ ROLASTAR/ALFA DUCT
5 | G.I. SHEET METAL DUCT | JINDAL HISSAR /NATIONAL/ TATA STEEL
6 | GRILLES/ DIFFUSERS/NOZZLES/DAMPER | RUSKIN TITUS/ SYSTEMAIR/TROX/CARYAIRE
7 | FIRE DAMPERS (UL LISTED & STAMPED) | GREENHECK/ RUSKIN/ TITUS/ SYSTEM AIR/ CARYAIRE
8 | CONTROL PANEL FOR MOTORIZED VCD | PROTON
9 | ACTUATOR FOR FIRE DAMPERS/MOTORIZED VCD | BELIMO, JOVENTA, SIEMENS
10 | G.I. SHEETS | JINDAL HISSAR/ SAIL
11 | FIRE RATING OF DUCTS | LAF/PROMAT
12 | FLEXIBLE DUCT | ATCO/ CARYAIRE
13 | SOUND ATTENUATOR | SYSTEMAIR/TROX/CARYAIRE
14 | GLASS WOOL/ FIBREGLASS | OWENS CORNING /U.P. TWIGA/ KIMMCO
15 | POLYURETHANE FOAM | MALANPUR /SUPERURETHANE
16 | CROSSED LINKED POLYETHYLENE FOAM | TROCELLENE / SUPREME/ PARAMOUNT/ THERMAFLEX/ K-FLEX
17 | CLOSED CELL ELASTOMERIC NITRILE RUBBER | K-FLEX /A-FLEX/ARMACELL
18 | NON-WOVEN FIBRE MATERIAL | MIKRON/ DU PONT
19 | UV PROTECTIVE COATING | ARMACELL/ARMACHEK/AMICOL/PARAMOUNT/ POLYBOND/PROMARK ASSOCIATES
20 | ALUMINUM TAPE | JOHNSON/BIRLA 3M
21 | ALUMINIUM SHEET/ PERFORATED AL SHEET | BALCO/ HINDALCO
22 | ANCHOR FASTNERS | CANNON/ HILTI/FICHER/RAWL PLUG
23 | VIBRATION ISOLATOR | CORI/RESISTOFLEX/DUNLUP
24 | FIRE SEALANT | BIRLA 3 M/ HILTI/PROMAT
25 | FLEXIBLE PIPE CONNECTION | CORI/RESISTOFLEX
26 | VAPOUR BARRIER COATING/PAINT | FOSTER SEAL PASS COATING
27 | FIBRE GLASS WOVEN CLOTH (7 MIL-APPROX. WT 200 GM./SQ.MT) | OWEN CORNING/ UP TWIGA/ KIMMCO/ARCO
28 | STUCK UP PINS | IDENDEN/ DURODYNE/ DETONATE
29 | PIPE HANGERS’ CLEVIS TYPE | GRINNELL/MUPRO/AMIL/UNISTRUT
30 | ONLINE TYPE VARIABLE AIR VOLUME BOXES | TRANE/HONEYWELL/JOHNSON CONTROL
31 | ACTUATOR FOR VAV | BELIMO/HONEYWELL
32 | CENTRIFUGAL FANS/PLUG FANS | KRUGER/NIKOTRA
33 | COPPER PIPING | MANDEV/RAJCO
34 | uPVC pipes & fittings | ASTRAL/ SUPREME/ ASHIRVAD/ FINOLEX
35 | DISTRIBUTION PANEL | NEPTUNE/ABB/ADLEC/ADVANCE
36 | MCB DISTRIBUTION BOARDS | SCHNEIDER/LEGRAND/SIEMENS/L & T
37 | BY-PASS TYPE VAV | COSMOS
38 | VARIABLE FREQUENCY DRIVES | DANFOSS/ABB/SIEMENS
39 | FILTERS | PUROLATOR/THERMODYNE/SPECTRUM
40 | TEMPERATURE AND RH SENSOR | HONEYWELL/SIEMENS-STAEFA/JOHNSON
41 | MOTORS | ABB/SIEMENS/BHARAT BIJLI
42 | VIBRATION ISOLATOR/SUSPENDERS | RESISTOFLEX
43 | FLEXIBLE CONNECTIONS FOR FAN OUTLET | MAPRO/CARYAIRE
43 | ELECTRONICS AIR CLEANERS | HONEYWELL/TRION/ZECO
44 | UVGI | HONEYWELL/ALFAA-UV/RUKS/ZECO
45 | CEMENT FIBRE SHEET | SHERA BOARD/BISON/EVEREST
46 | PLC AUTO SEQUENCER | PROTON
47 | PIPING (MS AND GI) | TATA STEEL/JINDAL (HISSAR)
48 | BUTTERFLY VALVES | ADVANCE/AUDCO
49 | BALL VALVES | RAPID COOL/EMRALD
50 | STRAINER | EMRALD/SANT
51 | PRESSURE GAUGE | EMRALD/FIEBIG/H-GURU
52 | WELDING ROD | ADVANI
53 | AUTO PURGE VALVES | ANERGY
54 | TEST POINT | ANERGY
55 | BTU METER | BELIMO/JOHNSON CONTROL/SONTEX
56 | PICV | BELIMO/JOHNSON CONTROL
LIST OF MAKES PL & FF
PLUMBING_SYSTEM
1 | Single bowl with drainboard sink | NIRALI / KAFF / EQUIVALENT
2 | Plumbing CP and sanitary fixtures, including flush valves, metering & manual faucets, Urinal,Urinal sensor ,shower line drain, Towel shelf,rain shower, sink mixture etc. | KOHLER / EURONICS / JAQUAR
3 | C.P gratings, floor drains and cockroach traps. | NEER / CHILLY / CAMARY
4 | Grab Bar,baby diaper changing station,robe hook Automatic & Manual soap dispencer,hand drayer,paper towel dispencer,Toilet paper holder. | EURONICS/ EQUIVALENT
5 | Floor drains | SUPREME / KOHLER/ NEER
6 | cPVC Pipe & Fittings for Water Supply | ASTRAL / SUPREME / ASHIRVAD
7 | uPVC pipes & fittings | ASTRAL/ SUPREME/ ASHIRVAD/ FINOLEX
8 | RCC Hume Pipes | INDIAN HUME PIPE / EQUIVALENT
9 | Solvent Cement | ASTRAL / SUPREME / PRINCE
10 | PVC ASTM Schedule pipe | ASTRAL / SUPREME/ EQUIVALENT
11 | Insulation ( Hot water ) | ARMAFLEX / VIDOFLEX /EQUIVALENT
12 | Brass & Gun metal, Gate valve | ZOLOTO / RB / SANT/ L&T
13 | Ball Valves | ZOLOTO / ITAP/ EQUIVALENT/ L&T
14 | Butterfly Valves | ZOLOTO / AUDCO/ EQUIVALENT/L&T
15 | Auto Sensors | AOS / ASKON/ EQUIVALENT
16 | Water meter ( Mechanical Type) | ITRON / KAYCEE / CAPSTAN / KRANTI
17 | Pipe Supports | HITECH/ EQUIVALENT
18 | Paints | ASIAN PAINTS / BERGER / SHALIMAR PAINTS
19 | Prefabricated, Fiberglass, Steel, PVC Etc. for Flushing Tank and Holding Tank, Overhead water Tank) | BELCO / RHINO / SINTEX
FIRE FIGHTING SYSTEM
20 | Pipe And Fittings | TATA/ JINDAL/ SURYA
21 | Valves | KBL/ INTERVALVE/ LEADER / SANT / ZOLOTO
22 | Pressure Gauge | H GURU / FIEBG / DANFOSS
23 | Flow Switches | DANFOSS / HONEYWELL / SWITZER
24 | Coating & Wrapping | IWL / RUSTEK / EQUIVALENT / PYPKOTE/ COALTECK
25 | Enamel Paint | ASIAN/ NEROLAC/ BERGER
26 | Paint Primers | ASIAN/ JENSON NICHOLSON
27 | Sprinklers | H.D. FIRE / TYCO / VIKING
28 | Fire Extinguishers | PADMINI/ SUPEREX/ OMEX/ MINIMAX / NEWAGE / GETECH / SAFEGUARD/ FIREX/ LIFEGUARD
29 | Pipe Hangers | CAMRY/ CHILLY/ GMGR
30 | Sprinkler Flexible Connection Pipe | NEWAGE/YOUNGJIN/FLEXHEAD