## HVAC
PROJECT : AMD, CIP LOUNGE AT T1, AHEMDABAD AIRPORT
Date | October' 27, 2023
S.NO | ITEM DESCRIPTION | UNIT | QTY. | Rate (INR) |  |  | Amount (INR) |  |  | QTY. | Rate (INR) |  |  | Amount (INR)
| SUB HEAD I - AIR-CONDITIONING SYSTEM |  |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
1.0 | EQUIPMENT
1.1 | FLOOR MOUNTED AIR HANDLING UNIT UVGI AND MERV-13
Supplying, installing, testing and commissioning of chilled water based double skin construction draw thru type Air Handling Unit (AHU) as per specification, each complete with following:
Inner skin of casing shall be constructed out of 24 gauge plain GS sheet & outer skin in 24 gauge pre-plasticized GS sheet sandwitched between 50mm thick injected PU foam insulation of density not less than 40 Kg /CuM and complete with inspection doors including control wiring as required. AHU shall have access for all parts
Fan section shall be complete with Plug fans. Fan should be suitable for VFD operation. All fans shall be AMCA certified.
Pre filter (MERV 8), 50mm thick washable synthetic fibre filter, face velocity not exceeding 500FPM. AHU shall be provided with MERV-13 filters (Bag type filter).
Six row deep cooling coil of copper tube, copper header and aluminum fins sized at maximum face velocity of 500 fpm. Cooling coil frame work and coil end plate shall be of SS304 construction. Wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge stainless steel duly insulated as per specifications.
Squirrel cage induction motors, IP-55, IE-3 suitable for 415 ± 10% volts, 50 Hz, AC supply meeting criterion as per ASHRAE standard 90.1-2013 and 90% or higher efficiency, suitable for VFD operation.
AHUs shall be complete with vibration isolation arrangement, rubber grooments etc to make installation vibration free.
Fan outlet velocity not exceeding 10.16 mps.
Total static pressure & motor rating shall be determined by contractor in co-ordination with manufacturer considering pressure drop across all accessories on supply air streams as per final appoved shop drawings.
Sound level at 1 m distance not exceeding 55 dB(A).
Starter panel for AHU and necessary electrical and control cables from starter panel to AHU shall be inclusive with AHU.
AHU shall be provided complete with doors to access the AHU parts. Contractor has to submit the AHU GA drawing showing piping connection side, door size, AHU size etc. Technical submittal for the same has to be approved from the consultants prior to procurement.
UVGI Specifications
AHU UVGI system with all accessories and framework required to mark fully functional in AHU’s for maintaining indoor Air Quality & Deep Coil Cleaning. Quantities of UVGI Lams shall be selected to cover entire cooling coil area with even distribution of light. The UVGI Equipment shall be listed to UL/CE Certified for electrical and fire & safety. UVGI system supplied must be in strict conformity with the specifications. The lamp shall have 9000 hrs. life, ballasts shall be electronic type, life rated greater > 14000 hrs. The UV system shall be installed on upstream side of cooling coil to avoid wind-chill effect. The UV emitters must be suitable for high airflow and low temperature operation. UV lamps should be operated in 254 nM wavelength, minimum intensity of UV light at surface of cooling coil shall be greater than 500 uW/cm2. UVGI system should be equipped with microprocessor-based control panel and shall have feature of run hour monitoring, Lamp fault Status, BMS compatibility. UVGI’s shall be suitable for following AHU Unit CFM.
AHU Capacity S.P Motor Rating Rows Area to be
No. (Cfm/TR) (mmWG) (HP) of coils fed
| AHU-1 20210/37TR 55 15 6 Lounge Area | No | 1 | 721050 | 114715 | 835765 | 721050 | 114715 | 835765 | 1 | 624797.43 | 104663.5 | 729460.93 | 624797.43 | 104663.5 | 729460.93
1.2 | VARIABLE FREQUENCY DRIVES (VFDs)
Supply, Installation, Testing and Commissioning of variable frequency drives for following Air Handling Units. Variable frequency drives shall be provided with necessary sensors and transmitters complete with control wiring in all respect as required and as per specifications. VFDs shall have built-in harmonic filters. The drives shall be suitable for the mentioned/approved motor rating. VFDs shall be housed in precoated, vandal proof enclosure with On/Off Push Buttons, Phase indication lights, A/M Switch and with adequate provisions for ventilation using a fan. The VFDs shall be able to receive the signals from multiple/combination of duct static pressure sensors/Temp. sensors and to ramp the speed of the motor.VFDs shall be suitable to take feed back and connectivity from all the DPS as mentioned below against each motor rating to facilitate averaging activity by VFD. Quoted price shall be inclusive of return air temperature sensor and necessary electrical switches including change over switch & copper cabling for integration with the AHU panel. VFDs shall be installed within Electrical panels as described under Section 'Electrical Works'. Overall protection of VFDs with Panels shall be IP-54.
(i) Sensing Range : 10mm to 50 mm WG
(ii) Output Signal : 4 mA to 20 mA
OR
0 V to 10 V DC
AHU Capacity Motor Rating Area to be
No. (Cfm) (HP) fed
| AHU-1 20210 15.0 Lounge Area | No | RO | 147200 | 28750 | 175950 |  |  |  | RO | 147200 | 28750 | 175950
1.2 | VENTILATION FANS
1.2.1 | INLINE FANS WITHOUT FILTER
Supply, installation, testing and commissioning of duct mounted IN-LINE FANS for exhaust air as shown in drawings. Each fan shall be complete with motor, mounting flanges, accessories like bird screen, fixed louvers and GI sheet canopy for weather protection as required. Quoted price shall be inclusive of electronic speed regulator and wiring between fan & speed regulator for single phase fans. Incase of 3 phase fans quoted price shall be inclusive of DOL starter panel with cabling between starter panel and fan.
Quoted prices shall be inclusive of all necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling with painting with one coat of primer and two coats of paint to supports of MS work. In addition, 18G GI sheet canopy work and vibration isolator pads to make installation vibration free for fans to be installed on terrace.
| Fan Selection arrangement shall be as follows: |  |  |  |  | 0 | [6 empty] | 0
| Fan Capacity S.P Area to |  |  |  |  | 0 | [6 empty] | 0
| No. (Cfm) (mmWG) to be exhausted |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
a. | IF-1(Circular) 500 16-17 Toilets adjoing live display kitchen | No | 1 | 12017 | 3825 | 15842 | 12017 | 3825 | 15842 | 1 | 12000 | 3635 | 15635 | 12000 | 3635 | 15635
b. | IF-2(Rectangular) 1200 14-15 Male, Female and Disabled Toilet | No | 1 | 33320 | 4915 | 38235 | 33320 | 4915 | 38235 | 1 | 33000 | 4800 | 37800 | 33000 | 4800 | 37800
c. | IF-3(Rectangular) 1000 14-15 Veg & Non Veg Kitchen | No | 0 | 32775 | 5175 | 37950 |  |  | 0 | 0 | 32775 | 5175 | 37950 |  |  | 0
[6 empty] | 0 |  |  | 0 |  |  |  | 0 |  |  | 0
e. | IF-4(Circular) 1000 10-12 Live Display Kitchen | No | 1 | 31140 | 4915 | 36055 | 31140 | 4915 | 36055 | 1 | 31140 | 4915 | 36055 | 31140 | 4915 | 36055
f. | IF-5(Circular) 125 10-12 Electrical Room | No | 0 | 9660 | 2300 | 11960 |  |  | 0 | 0 | 9660 | 2300 | 11960 |  |  | 0
| Contactor to check/calculate static pressure drop as per shop drawing. |  |  |  |  | 0 | [6 empty] | 0
| Note: Cigar Room Inline fan will be low noise type, sound level should not exceed 40dBA @ 2meters. Selection for the same to be done accordingly. |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
1.2.2 | INLINE FANS WITH FILTER |  |  |  |  | 0 | [6 empty] | 0
| Supply, installation, testing and commissioning of duct mounted IN-LINE FANS for fresh air as shown in drawings. Each fan shall be complete with motor, mounting flanges, accessories like bird screen, fixed louvers and GI sheet canopy for weather protection as required. Quoted price shall be inclusive of electronic speed regulator and wiring between fan & speed regulator for single phase fans. Incase of 3 phase fans quated price shall be inclusive of DOL starter panel with cabling between starter panel and fan. |  |  |  |  | 0 | [6 empty] | 0
| All fans shall be provided with Pre-Filter section (MERV-8) complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 450 FPM. |  |  |  |  | 0 | [6 empty] | 0
| Quoted prices shall be inclusive of all necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling with painting with one coat of primer and two coats of paint to supports of MS work. Fans feeding/exhausting to the same areas shall be integrated. In addition, 18G GI sheet canopy work and vibration isolator pads to make installation vibration free for fans to be installed on terrace. |  |  |  |  | 0 | [6 empty] | 0
| Fan Selection arrangement shall be as follows: |  |  |  |  | 0 | [6 empty] | 0
| Fan Capacity S.P Area to |  |  |  |  | 0 | [6 empty] | 0
| No. (Cfm) (mmWG) to be exhausted |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
a. | IF-6(Rectangular) 1000 20-22 Live Display kitchen | No | 0 | 38525 | 5175 | 43700 |  |  | 0 | 0 | 38525 | 5175 | 43700 |  |  | 0
b. | IF-7(Rectangular) 1000 20-22 Veg & Non. Veg kitchen | No | 0 | 38525 | 5175 | 43700 |  |  | 0 | 0 | 38525 | 5175 | 43700 |  |  | 0
| Contactor to check/calculate static pressure drop as per shop drawing. |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| TOTAL ITEM NO. 1 (EQUIPMENT) |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
2.0 | PIPING AND VALVES |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
2.1 | CHILLED WATER PIPING |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Supply , Installation, Testing and Commissioning of MS heavy class (Class "C') pipes cut to requird lengths and installed with all welded joints. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers, sockets etc., and hanging arrangement and floor supports as required, rigid PUF saddles, washers and check nuts etc in accordance with the approved shop drawings and specifications. All sleeves in Fire wall/slab shall be sealed using fireproof sealant. Pipes shall be of following sizes : |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| For Pipe sizes of 80mm dia & above complete "C" channel support shall be provided. For floor supports, supports shall be complete with pipes of adequate size with base plate & vibration isolation pads and "C" channel. All pipe supports channels, fastner etc. to be selected as per support depth & loading as per structural consultant recommendations. |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
a. | 80mm dia | RM | 4 | 1912 | 600 | 2512 | 7648 | 2400 | 10048 | 4 | 1912 | 600 | 2512 | 7648 | 2400 | 10048
b. | 65mm dia | RM | - | 1840 | 575 | 2415 |  |  | Rate Only | - | 1840 | 575 | 2415 |  |  | Rate Only
[6 empty] | 0 | [6 empty] | 0
2.2 | CONDENSATE DRAIN PIPING -GI |  |  |  |  | 0 | [6 empty] | 0
| Supply, Installation , Testing and Commissioning |  |  |  |  | 0 | [6 empty] | 0
| of GI medium class (Class 'B') pipes cut to requird |  |  |  |  | 0 | [6 empty] | 0
| lengths and installed with all screwed joints |  |  |  |  | 0 | [6 empty] | 0
| for condensate drain. Quoted price |  |  |  |  | 0 | [6 empty] | 0
| shall be inclusive of supply and fixing in |  |  |  |  | 0 | [6 empty] | 0
| position the necessary fittings like elbows, tees |  |  |  |  | 0 | [6 empty] | 0
| reducers etc., and supporting arrangement |  |  |  |  | 0 | [6 empty] | 0
| in accordance with the approved shop drawings |  |  |  |  | 0 | [6 empty] | 0
| and specifications.Pipes shall be insulated with |  |  |  |  | 0 | [6 empty] | 0
| 9mm thick closed cell elastomeric insulation |  |  |  |  | 0 | [6 empty] | 0
| in tubing form . Pipes shall be of following sizes : |  |  |  |  | 0 | [6 empty] | 0
a. | 50mm dia | RM | 3 | 1205 | 395 | 1600 | 3615 | 1185 | 4800 | 3 | 1205 | 395 | 1600 | 3615 | 1185 | 4800
b. | 40mm dia | RM | - | 1093 | 345 | 1438 |  |  | Rate Only | - | 1040 | 345 | 1385 |  |  | Rate Only
[6 empty] | 0 | [6 empty] | 0
2.3 | BUTTERFLY VALVES |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Providing and fixing in position the following wafer type Butterfly Valves complete with SS-410 disc, companion flanges, nuts, bolts, gaskets etc. as required. Butterfly valves shall confirm to PN -16 rating as per specifications. Quoted price shall be inclusive of insulation for valves associated with chilled water circuit as per the specifications. The valves shall be following sizes. |  |  |  |  | 0 | [6 empty] | 0
a. | 80mm dia | No | 0 | 5750 | 1725 | 7475 |  |  | 0 | 0 | 5750 | 1725 | 7475 |  |  | 0
b. | 65mm dia | No | - | 5520 | 1495 | 7015 |  |  |  | - | 5520 | 1495 | 7015
[6 empty] | 0 | [6 empty] | 0
2.4 | BALL VALVES (for AHUs) |  |  |  |  | 0 | [6 empty] | 0
| Supplying , Installaing , Testing and Commissioning |  |  |  |  | 0 | [6 empty] | 0
| of following Ball Valves in accordance with |  |  |  |  | 0 | [6 empty] | 0
| the approved shop drawings and specifications. |  |  |  |  | 0 | [6 empty] | 0
| Quoted price shall be inclusive of insulation as per the specifications. |  |  |  |  | 0 | [6 empty] | 0
a. | 40mm dia | No | - | 3910 | 920 | 4830 |  |  | Rate Only | - | 3910 | 920 | 4830 |  |  | Rate Only
b. | 32mm dia | No | - | 3450 | 920 | 4370 |  |  | Rate Only | - | 3450 | 920 | 4370 |  |  | Rate Only
[6 empty] | 0 | [6 empty] | 0
2.5 | BALANCING VALVES |  |  |  |  | 0 | [6 empty] | 0
| Supplying , Installaing , Testing and Commissioning of following Balancing Valves in accordance with the approved shop drawings and specifications. Balancing valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation as per the specifications. |  |  |  |  | 0 | [6 empty] | 0
a. | 80mm dia | No | - | 39675 | 1725 | 41400 |  |  | Rate Only | - | 39675 | 1725 | 41400 |  |  | Rate Only
b. | 50mm dia | No | - | 34155 | 1495 | 35650 |  |  | Rate Only | - | 34155 | 1495 | 35650 |  |  | Rate Only
[6 empty] | 0 | [6 empty] | 0
2.6 | 2/3 WAY DIVERTING VALVES (for AHUs ) |  |  |  |  | 0 | [6 empty] | 0
| Supply , Installation , Testing and Commissioning |  |  |  |  | 0 | [6 empty] | 0
| of motorised 2/3 way diverting valves with |  |  |  |  | 0 | [6 empty] | 0
| modulating motor, proportional thermostat and |  |  |  |  | 0 | [6 empty] | 0
| copper control wiring for air handling units. |  |  |  |  | 0 | [6 empty] | 0
| Quoted price shall be inclusive of current transformers, |  |  |  |  | 0 | [6 empty] | 0
| control cabling etc. as required and insulation as per |  |  |  |  | 0 | [6 empty] | 0
| specifications. The valves shall be of the following sizes : |  |  |  |  | 0 | [6 empty] | 0
a. | 80mm dia valves | No | - | 48875 | 2875 | 51750 |  |  | Rate Only | - | 48875 | 2875 | 51750 |  |  | Rate Only
b. | 65mm dia valves | No | - | 37950 | 2300 | 40250 |  |  | Rate Only | - | 37950 | 2300 | 40250 |  |  | Rate Only
[6 empty] | 0 | [6 empty] | 0
2.7 | AUTO PURGE VALVES |  |  |  |  | 0 | [6 empty] | 0
| Supplying , Installaing , Testing and Commissioning |  |  |  |  | 0 | [6 empty] | 0
| of 10mm dia automatic purge valves. | No | 0 | 3220 | 1150 | 4370 |  |  | 0 | 0 | 3220 | 1150 | 4370 |  |  | 0
[6 empty] | 0 | [6 empty] | 0
2.8 | Y- STRAINER FOR AHUs |  |  |  |  | 0 | [6 empty] | 0
| Supplying , Installaing , Testing and Commissioning |  |  |  |  | 0 | [6 empty] | 0
| of following 'Y'- strainers for AHUs as per the |  |  |  |  | 0 | [6 empty] | 0
| specifications having PN-16 rating. Quoted price shall be |  |  |  |  | 0 | [6 empty] | 0
| inclusive of insulation as per the specifications. |  |  |  |  | 0 | [6 empty] | 0
a. | 80mm dia valves | No | 0 | 7475 | 1150 | 8625 |  |  | 0 | 0 | 7475 | 1150 | 8625 |  |  | 0
b. | 65mm dia valves | No | - | 6670 | 1035 | 7705 |  |  |  | - | 6670 | 1035 | 7705
[6 empty] | 0 | [6 empty] | 0
2.9 | THERMOMETERS |  |  |  |  | 0 | [6 empty] | 0
| Supplying , Installaing , Testing and Commissioning |  |  |  |  | 0 | [6 empty] | 0
| of 100mm dia dial type thermometers as per the |  |  |  |  | 0 | [6 empty] | 0
| specifications. | No | 0 | 4600 | 1150 | 5750 |  |  | 0 | 0 | 4600 | 1150 | 5750 |  |  | 0
[6 empty] | 0 | [6 empty] | 0
2.1 | PRESSURE GAUGES |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Supply , Installation , Testing and Commissioning of industrial type pressure gauges completely in stainless stainless steel (SS) construction with 100mm dia dial and complete with shut off gauge cocks etc. as per the specifications.U tube of pressure gauges shall be insulated. | No | 0 | 3680 | 1150 | 4830 |  |  | 0 | 0 | 3680 | 1150 | 4830 |  |  | 0
[6 empty] | 0 | [6 empty] | 0
2.11 | BTU METER |  |  |  |  | 0 | [6 empty] | 0
| The BTU meter should be a combined heat and cold type static meter using Non-Mechanical (Ultrasonic/Oscillating Jet) measurement principle. The nominal pressure rating should be PN16, IP54 protection. The meter should conform in all aspects to MID certification EN 1434 class2/3. Data logging minimim upto 12 months. The meter (Calculator) shall have an NFC communication. The Calculator to have Battery backup minimum up to 2 months in case of complete power failure and shell life of 10years, 230VAC or 24VAC/VDC power supply operated with integrated Bacnet/modbus module/cloud. |  |  |  |  | 0 | [6 empty] | 0
a. | 80mm dia valves | No | 0 | 148925 | 6325 | 155250 |  |  | 0 | 0 | 148925 | 6325 | 155250 |  |  | 0
b. | 65mm dia valves | No | - | 138000 | 5750 | 143750 |  |  | Rate Only | - | 138000 | 5750 | 143750 |  |  | Rate Only
[6 empty] | 0 | [6 empty] | 0
2.12 | Supply, Installation, testing and commissioning of electronic, AUTOMATIC PRESSURE INDEPENDENT BALANCING VALVE type dynamic balancing Valve with integrated 2 way modulating Control valves in a single body. The actuator shall be capable of accepting 2-10VCD, 4- 20 mA electric signal and shall provide similar transduced feedback output signal to control system. The valves & actuators shall be compatible with Building Automation System. HVAC contractor shall ensure the required power supply to the valve for proper working.The minimum close off Pressure of actuator must be 1.5 times shut off head of pump . The valve shall be suitable for following pipe sizes: |  |  |  |  | 0 | [6 empty] | 0
a. | 80mm dia valves | No | - | 133975 | 4025 | 138000 |  |  | Rate Only | - | 133975 | 4025 | 138000 |  |  | Rate Only
b. | 65mm dia valves | No | 0 | 105800 | 3450 | 109250 |  |  | 0 | 0 | 105800 | 3450 | 109250 |  |  | 0
c. | 50mm dia valves | No | - | 98900 | 3450 | 102350 |  |  | Rate Only | - | 98900 | 3450 | 102350 |  |  | Rate Only
[6 empty] | 0 | [6 empty] | 0
2.13 | BMS INTERFACE |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Necessary sockets and nipples with shut off valves for mounting sensors/transmitters on pipe line to interface the BMS system. |  |  |  |  | 0 | [6 empty] | 0
|  | Lot |  | 11500 | 46000 | 57500 |  |  |  |  | 11500 | 46000 | 57500
| TOTAL ITEM NO. 2 (PIPING AND VALVES) |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
3 | AIR DISTRIBUTION |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
3.1 | Supply, installation and testing of SITE Fabricated GI sheet metal ducts as per IS-655 Standard in accordance with the approved shop drawings as required by the specifications. Quoted price shall be inclusive of all necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and two coats of paint to supports of MS work. Quoted price shall be inclusive of scaffolding work as required. Note:All exposed surfaces & duct shall be painted in black mat finish by the HVAC contractor. |  |  |  |  | 0 | [6 empty] | 0
3.1.1 | 24 gauge galvanised sheet steel (0.63 mm) | Sqm. | 892 | 1147 | 437 | 1584 | 1023124 | 389804 | 1412928 | 892 | 1090 | 415 | 1505 | 972280 | 370180 | 1342460
3.1.2 | 22 gauge galvanised sheet steel (0.8 mm) | Sqm. | 345 | 1315 | 437 | 1752 | 453675 | 150765 | 604440 | 345 | 1250 | 415 | 1665 | 431250 | 143175 | 574425
3.1.3 | 20 gauge galvanised sheet steel (1.0 mm) | Sqm. | 60 | 1475 | 600 | 2075 | 88500 | 36000 | 124500 | 60 | 1401 | 570 | 1971 | 84060 | 34200 | 118260
3.1.4 | 18 gauge galvanised sheet steel (1.25 mm) | Sqm. | 60 | 1805 | 605 | 2410 | 108300 | 36300 | 144600 | 60 | 1715 | 575 | 2290 | 102900 | 34500 | 137400
[6 empty] | 0 | [6 empty] | 0
3.2 | Supply, Installation,Testing and Balancing of flexible ducting comprising of inner as well as outer skin constructed out of aluminium & fibre glass insulation 25mm thick of minimum 24 kg/cu.m density insulation sandwitched in between. Duct should confirm to fire rating standards BS-476 part 5, 6 & 7. Flexible Ducts of following sizes as per approved shop drawings, specifications : |  |  |  |  | 0 | [6 empty] | 0
3.2.1 | 350 mm dia. | Mtr. | RO | 805 | 173 | 978 |  |  |  | RO | 805 | 173 | 978
3.2.2 | 300 mm dia. | Mtr. | 35 | 655 | 165 | 820 | 22925 | 5775 | 28700 | 35 | 655 | 165 | 820 | 22925 | 5775 | 28700
3.2.3 | 200 mm dia. | Mtr. | 12 | 546 | 165 | 711 | 6552 | 1980 | 8532 | 12 | 546 | 165 | 711 | 6552 | 1980 | 8532
3.2.4 | 150 mm dia. | Mtr. | 12 | 495 | 140 | 635 | 5940 | 1680 | 7620 | 12 | 495 | 140 | 635 | 5940 | 1680 | 7620
3.2.5 | 100 mm dia. | Mtr. | 12 | 460 | 145 | 605 | 5520 | 1740 | 7260 | 12 | 460 | 145 | 605 | 5520 | 1740 | 7260
[6 empty] | 0 | [6 empty] | 0
3.3 | Supply, installation and testing of GI construction Opposed blade Volume control dampers within ducts to be provided with suitable ducts lever and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | Sqm. | 5 | 7975 | 1315 | 9290 | 39875 | 6575 | 46450 | 5 | 7975 | 1315 | 9290 | 39875 | 6575 | 46450
[6 empty] | 0 | [6 empty] | 0
3.4 | Supply, installation, testing and commissioning of Motorised combined smoke & fire damper complete with control panel, inter connecting wiring at locations shown in approved shop drawings and as per specifications. |  |  |  |  | 0 | [6 empty] | 0
3.4.1 | Smoke & Fire Dampers. | Sqm. | 5.5 | 26000 | 1315 | 27315 | 143000 | 7232.5 | 150232.5 | 5.5 | 24700 | 1250 | 25950 | 135850 | 6875 | 142725
3.4.2 | Control Panel & Wiring (including actuators) | No | 8 | 13656 | 2185 | 15841 | 109248 | 17480 | 126728 | 8 | 13656 | 2075 | 15731 | 109248 | 16600 | 125848
[6 empty] | 0 | [6 empty] | 0
3.5 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply Air Grilles with multiblade type key operated grille louver dampers in accordance with the approved shop drawings and specifications. | Sqm. | 7 | 12565 | 1095 | 13660 | 87955 | 7665 | 95620 | 7 | 12020 | 1095 | 13115 | 84140 | 7665 | 91805
[6 empty] | 0 | [6 empty] | 0
3.6 | Supply, installation, testing and balancing of powder coated extruded Aluminium Exhaust/Return Air Grilles without multiblade type grille louver dampers | Sqm. | 10 | 8195 | 1095 | 9290 | 81950 | 10950 | 92900 | 10 | 7785 | 1095 | 8880 | 77850 | 10950 | 88800
[6 empty] | 0 | [6 empty] | 0
3.7 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape Supply Air Diffusers with removable core & anti smudge ring & key operated volume control dampers as per approved drawings and specifications. | Sqm. | 3 | 14750 | 1640 | 16390 | 44250 | 4920 | 49170 | 3 | 14015 | 1640 | 15655 | 42045 | 4920 | 46965
[6 empty] | 0 | [6 empty] | 0
3.8 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape Return Air Diffusers as per approved drawings and specifications. | Sqm. | 3 | 12345 | 765 | 13110 | 37035 | 2295 | 39330 | 3 | 12350 | 765 | 13115 | 37050 | 2295 | 39345
[6 empty] | 0 | [6 empty] | 0
3.9 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction. Louvers with bird screen for exhaust air as per specifications and approved drawings. | Sqm. | 2.5 | 15625 | 765 | 16390 | 39062.5 | 1912.5 | 40975 | 2.5 | 14745 | 730 | 15475 | 36862.5 | 1825 | 38687.5
[6 empty] | 0 | [6 empty] | 0
3.1 | Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 6 | 1860 | 875 | 2735 | 11160 | 5250 | 16410 | 6 | 1860 | 875 | 2735 | 11160 | 5250 | 16410
[6 empty] | 0 | [6 empty] | 0
3.11 | Supply, Installation and Testing of single piece GI round spigot made out of spinning process with 50mm height and having grooves on both sides and circular flanges. Spigots shall be installed on main ducts to facilitate connection of flexible ducts. |  |  |  |  | 0 | [6 empty] | 0
3.11.1 | 350 mm dia. | Nos. | RO | 1207.5 | 518 | 1725.5 |  |  |  | RO | 1207.5 | 518 | 1725.5
3.11.2 | 300 mm dia. | Nos. | 35 | 985 | 440 | 1425 | 34475 | 15400 | 49875 | 35 | 985 | 440 | 1425 | 34475 | 15400 | 49875
3.11.3 | 200 mm dia. | Nos. | 12 | 875 | 440 | 1315 | 10500 | 5280 | 15780 | 12 | 875 | 440 | 1315 | 10500 | 5280 | 15780
3.11.4 | 150 mm dia. | Nos. | 12 | 765 | 330 | 1095 | 9180 | 3960 | 13140 | 12 | 765 | 330 | 1095 | 9180 | 3960 | 13140
3.11.5 | 100 mm dia. | Nos. | 12 | 765 | 330 | 1095 | 9180 | 3960 | 13140 | 12 | 765 | 330 | 1095 | 9180 | 3960 | 13140
[6 empty] | 0 | [6 empty] | 0
3.12 | Supply, Installation and Testing of Butterfly damper of aluminium sheet construction with two flap with sleeve as per thespecifications and shop drawings. |  |  |  |  | 0 | [6 empty] | 0
3.12.1 | 350 mm dia. | Nos. | RO | 3508 | 518 | 4026 |  |  |  | RO | 3508 | 492 | 4000
3.12.2 | 300 mm dia. | Nos. | 35 | 3060 | 440 | 3500 | 107100 | 15400 | 122500 | 35 | 2900 | 420 | 3320 | 101500 | 14700 | 116200
3.12.3 | 200 mm dia. | Nos. | 12 | 2625 | 440 | 3065 | 31500 | 5280 | 36780 | 12 | 2625 | 420 | 3045 | 31500 | 5040 | 36540
3.12.4 | 150 mm dia. | Nos. | 12 | 2405 | 330 | 2735 | 28860 | 3960 | 32820 | 12 | 2405 | 330 | 2735 | 28860 | 3960 | 32820
3.12.5 | 100 mm dia. | Nos. | 12 | 2075 | 330 | 2405 | 24900 | 3960 | 28860 | 12 | 2075 | 330 | 2405 | 24900 | 3960 | 28860
[6 empty] | 0 |  |  | 0 |  |  |  | 0
3.13 | MOTORIZED VCD |  |  |  |  | 0 | [6 empty] | 0
| Supply, Installation, Testing and commissioning of multi box type zero leakage extruded aluminium dampers for ducts to be provided with suitable links, levers and quadrants for manual ON/OFF and control of air flow as per approved shop drawing and specifications. | Sqm | RO | 19550 | 1725 | 21275 |  |  |  | RO | 19550 | 1725 | 21275
| Supply and fixing of actuators of suitable rating of torque complete with control panel and manual switch, transformer, copper wiring from junction box and actuator associated with the above VCDs. Actuator shall be suitable for duct size as shown in the drawing. Quoted arrangement shall be inclusive of all arrangement requited to ON/OFF the actuator/VCD integrated with switch to shut/on the supply air to digital immersive room. | No | RO | 18975 | 2300 | 21275 |  |  |  | RO | 18975 | 2300 | 21275
3.14 | THERMAL INSULATION
3.14.1 | THERMAL INSULATION FOR DUCTWORK
Supply and Application of external thermal insulation of supply /return air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Quoted price shall be inclusive of adhesive, tapes as per specification. insulation shall be provided with aluminium foil, factory laminated.
Insulation thickness/application will be as per approved shop drawing notes.
a. | 25 mm thick | Sqm | 25 | 1095 | 220 | 1315 | 27375 | 5500 | 32875 | 25 | 1095 | 220 | 1315 | 27375 | 5500 | 32875
b. | 19 mm thick | Sqm | RO | 1070 | 196 | 1266 |  |  | 0 | RO | 1070 | 196 | 1266 |  |  | 0
c. | 16 mm thick | Sqm | 25 | 910 | 185 | 1095 | 22750 | 4625 | 27375 | 25 | 910 | 185 | 1095 | 22750 | 4625 | 27375
d. | 13 mm thick | Sqm | 875 | 820 | 165 | 985 | 717500 | 144375 | 861875 | 875 | 820 | 165 | 985 | 717500 | 144375 | 861875
e. | 9 mm thick | Sqm | 75 | 710 | 165 | 875 | 53250 | 12375 | 65625 | 75 | 710 | 165 | 875 | 53250 | 12375 | 65625
3.14.2 | ACOUSTIC LINING OF DUCTS
Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet.
a. | 10mm thick lining | SqM | 25 | 13495 | 165 | 13660 | 337375 | 4125 | 341500 | 25 | 13495 | 165 | 13660 | 337375 | 4125 | 341500
b. | 25mm thick lining | SqM | 120 | 1750 | 220 | 1970 | 210000 | 26400 | 236400 | 120 | 1750 | 220 | 1970 | 210000 | 26400 | 236400
3.14.3 | CHW PIPE INSULATION
Using Class 'O' Closed Cell Elastomeric Insulation
Supply and Application of 25mm/32mm thick closed cell elastomeric insulation in tubing form for chilled water piping as per the specifications. Quoted price shall be inclusive of adhesive as per specifications. Joints shall be sealed with adhesive forming proper bonding. Quoted price shall be inclusive of 24 G aluminium cladding for chilled water piping.
a. | 80mm dia (25mm thick) | RM | 10 | 1475 | 492 | 1967 | 14750 | 4920 | 19670 | 10 | 1475 | 492 | 1967 | 14750 | 4920 | 19670
b. | 65mm dia (25mm thick) | RM | - | 1437.5 | 460 | 1897.5 |  |  | Rate Only | - | 1437.5 | 460 | 1897.5 |  |  | Rate Only
c. | 50mm dia (25mm thick) | RM | - | 1437.5 | 345 | 1782.5 |  |  | Rate Only | - | 1437.5 | 345 | 1782.5 |  |  | Rate Only
3.15 | Air Transfer Grilles
| Supply, Installation and testing of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | 0.5 | 8050 | 1725 | 9775 | 4025 | 862.5 | 4887.5 | 0.5 | 8050 | 1725 | 9775 | 4025 | 862.5 | 4887.5
TOTAL ITEM NO. 3 (AIR DISTRIBUTION)
4 | UNDERDECK INSULATION FOR EXPOSED ROOF
| Supply and Application of 16mm thick closed cell nitrile rubber elastomeric insulation for exposed roof towards underdeck insulation. Quoted price shall be inclusive of Pidilite SR-505/998 adhesive as required and as per the specifications. | Sqm | 0 | 1035 | 288 | 1323 |  |  | 0 | 0 | 1035 | 288 | 1323 |  |  | 0
TOTAL ITEM NO. 4
5 | ONLINE TYPE VAV BOXES
5.1 | Supply Installation,Testing and Commissioning of On Line type variable air volume boxes complete with necessary controllers, Heating-Cooling digital thermostat, Damper actuator, multi point pick-up inlet Air Flow velocity, sensor and copper control wiring and necessary transformer, etc. as required and as per the specifications. VAV Boxes should be BMS compatible. VAV Boxes should be suitable to working on Cooling & Heating mode as per requirement.
VAV Box shall be of following design parameters :
Max. Air Qty. Min. Air Qty. Location
(Cfm) (Cfm)
a. | Upto 500 50 As shown on Drg. | No | RO | 25875 | 2875 | 28750 |  |  |  | RO | 25875 | 2875 | 28750
b. | From 525 to 1000 From 50 to 100 As shown on Drg. | No | RO | 26450 | 2875 | 29325 |  |  |  | RO | 26450 | 2875 | 29325
c. | From 1025 to 1500 From 100 to 150 As shown on Drg. | No | RO | 27025 | 2875 | 29900 |  |  |  | RO | 27025 | 2875 | 29900
d. | From 1525 to 2000 From 150 to 200 As shown on Drg. | No | RO | 27025 | 4025 | 31050 |  |  |  | RO | 27025 | 4025 | 31050
e. | From 2025 to 2500 From 200 to 250 As shown on Drg. | No | RO | 28750 | 4025 | 32775 |  |  |  | RO | 28750 | 4025 | 32775
f. | From 2525 to 3000 From 250 to 300 As shown on Drg. | No | RO | 31625 | 4025 | 35650 |  |  |  | RO | 31625 | 4025 | 35650
g. | From 3025 to 3500 From 300 to 350 As shown on Drg. | No | RO | 31625 | 5175 | 36800 |  |  |  | RO | 31625 | 5175 | 36800
h. | From 3525 to 4000 From 350 to 400 As shown on Drg. | No | RO | 35075 | 5175 | 40250 |  |  |  | RO | 35075 | 5175 | 40250
[6 empty] | 0 | [6 empty] | 0
5.2 | DUCT PRESSURE SENSORS |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Supply, Installation and Testing of pressure sensors to be installed in supply air ducts. Quoted price shall be inclusive of necessary conduting, copper control cabling from the sensors to the respective VFDs as per "Approved Shop Drawings". | No | RO | 2875 | 1150 | 4025 |  |  |  | RO | 2875 | 1150 | 4025
| TOTAL ITEM NO. 5 (ONLINE TYPE VAV BOXES) |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
6 | AHU ROOM ACOUSTIC LINING |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Supply and Application of acoustic/ thermal lining of walls/ceiling of AHU rooms using resin bonded fibre glass insulation of density not less than 32Kg/CuM as per the approved shop drawings and specifications. Quoted price shall be inclusive of GSS channel, metal screws, washers, fibre glass tissue, perforated sheet etc. as required for complete installation. |  |  |  |  | 0 | [6 empty] | 0
a. | 50mm thick lining | SqM | 90 | 1915 | 495 | 2410 | 172350 | 44550 | 216900 | 90 | 1820 | 470 | 2290 | 163800 | 42300 | 206100
TOTAL ITEM NO. 6 (AHU ROOM ACOUSTIC LINING)
| TOTAL SUB-HEAD I carried over to Summary | [7 empty] | 6057143 | [6 empty] | 5798153.93
SUB HEAD II -KITCHEN VENTILATION SYSTEM (COOKING KITCHEN)
1.0 | EQUIPMENT
1.1.1 | Supplying, installing, testing and commissioning of Double Skin construction (of similar specification as that of AHU without mixing chamber and thermal break profile) Air Washer unit with DIDW class-I centrifugal fan (Efficiency >75%), TEFC weather proof motor of IP55 protection at 415±10% volts, 3 phase, 50 cycles power and high efficiency(IE3), belt drive, multisheave pulley mounted on motor and fan shaft, belt guard, motor and fan mounted on common base with metallistik vibration isolators. Fan capacity shall be based on outlet velocity not exceeding 10.16 MPS and fan speed not exceeding 1000 RPM. Total static pressure & Motor ratings shall be checked by Vendor/Contractor based on ducting layout.
Supplying, installing, testing and commissioning of horizontal monobloc pumps (1 W + 1 Standby) of suitable rating, of Beacon weir/KEC make factory mounted on GI channel base with electric motor for circulation of water. Pumps shall be aligned and suitable for 415±10% volts, 50 cycle’s 3 phase power supply. One No. 3 phase isolator switch in weather proof enclosure shall be provided near motor
In addition, quoted price shall be inclusive of civil work/channel etc. required to install FFU along with proper 18G GI sheet canopy work and vibration isolator pads to make installation vibration free, flexible canvass connection. Price shall be inclusive of bird screen at inlet.
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
| AW-1 7000 40-45 1.5 Kitchen Area | No | 1 | 437000 | 81940 | 518940 | 437000 | 81940 | 518940 | 1 | 400000 | 70000 | 470000 | 400000 | 70000 | 470000
1.1.2 | Supply , Installation , Testing and Commissioning of wet type scrubber (packaged type) comprising of following as per the specifications :
Fan section complete with backward curved DIDW type centrifugal fan/s, TEFC squirrel cage induction motor (IE3) suitable to operate on 415+10%V, 50Hz, 3 phase AC power supply and belt drive package. Casing of wet type scrubber shall be constructed out of 16 gauge GS sheet complete with inspection doors as required. Centrifugal fans shall be coated with epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS).
Wet section complete with double bank spray header in GI construction and nozzles, louvers PVC mist eliminators & mist collection tray made out of 16G GSS, strainer of fine mesh brass screen, globe valve, float valve, quick fill, over flow & drain connections, GI medium class piping and 3 phase monobloc pump of 0.5HP motor rating(1 W + 1 Standby) as required according to the capacity of scrubber machines. Wet section including sump will be made of 1.25mm thick SS-304 A grade stainless steel .
In addition, quoted price shall be inclusive of civil work/channel etc. required to install FFU along with proper 18G GI sheet canopy work and vibration isolator pads to make installation vibration free, flexible canvass connection.
The Scrubber Machines (EAC) shall be of following duty parameters :
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
| AS-1 7000 50 2 Kitchen Area | No | 1 | 1999275 | 131100 | 2130375 | 1999275 | 131100 | 2130375 | 1 | 1609401.08 | 120000 | 1729401.08 | 1609401.08 | 120000 | 1729401.08
| Note : Actual motor selection shall be done at manufacturer end. |  |  |  |  | 0 | [6 empty] | 0
| Contractor to calculate static pressure drop as per final installation within kitchen and approved shop drawing ductwork for Air Washer and Air-Scrubber |  |  |  |  | 0 | [6 empty] | 0
| TOTAL ITEM NO. 1 (EQUIPMENT) |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
2 | AIR DISTRIBUTION |  |  |  |  | 0 | [6 empty] | 0
2.1 | Supply, installation and testing of SITE Fabricated GI sheet metal ducts as per IS-655 Standard in accordance with the approved shop drawings as required by the specifications. Quoted price shall be inclusive of all necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and two coats of paint to supports of MS work Note:All exposed surfaces & duct shall be painted in black mat finish by the HVAC contractor. |  |  |  |  | 0 | [6 empty] | 0
2.1.1 | 24 gauge galvanised sheet steel (0.63 mm) | Sqm. | 280 | 1150 | 440 | 1590 | 322000 | 123200 | 445200 | 280 | 1050 | 420 | 1470 | 294000 | 117600 | 411600
2.1.2 | 22 gauge galvanised sheet steel (0.8 mm) | Sqm. | 6 | 1295 | 440 | 1735 | 7770 | 2640 | 10410 | 6 | 1250 | 420 | 1670 | 7500 | 2520 | 10020
2.1.3 | 20 gauge galvanised sheet steel (1.0 mm) | Sqm. | 6 | 1475 | 605 | 2080 | 8850 | 3630 | 12480 | 6 | 1450 | 575 | 2025 | 8700 | 3450 | 12150
2.1.4 | 18 gauge galvanised sheet steel (1.25 mm) | Sqm. | 6 | 1805 | 605 | 2410 | 10830 | 3630 | 14460 | 6 | 1800 | 575 | 2375 | 10800 | 3450 | 14250
2.2 | Supply, installation and testing of GI construction Opposed blade Volume control dampers within ducts to be provided with suitable ducts lever and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | Sqm. | 1.5 | 7975 | 1315 | 9290 | 11962.5 | 1972.5 | 13935 | 1.5 | 7575 | 1315 | 8890 | 11362.5 | 1972.5 | 13335
2.3 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape Supply Air Diffusers with removable core & anti smudge ring & key operated volume control dampers as per approved drawings and specifications. | Sqm. | 1.5 | 14750 | 1640 | 16390 | 22125 | 2460 | 24585 | 1.5 | 14750 | 1640 | 16390 | 22125 | 2460 | 24585
2.4 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape Return Air Diffusers as per approved drawings and specifications. | Sqm. | 1.5 | 15625 | 765 | 16390 | 23437.5 | 1147.5 | 24585 | 1.5 | 15625 | 765 | 16390 | 23437.5 | 1147.5 | 24585
2.5 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction. Louvers with bird screen for exhaust air as per specifications and approved drawings. | Sqm. | 2 | 12020 | 1640 | 13660 | 24040 | 3280 | 27320 | 2 | 12020 | 1640 | 13660 | 24040 | 3280 | 27320
2.6 | Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 2.5 | 1955 | 920 | 2875 | 4887.5 | 2300 | 7187.5 | 2.5 | 1955 | 920 | 2875 | 4887.5 | 2300 | 7187.5
[6 empty] | 0 | [6 empty] | 0
2.7 | THERMAL INSULATION |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
2.7.1 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) |  |  |  |  | 0 | [6 empty] | 0
| (Using Factory Laminated fibre glass insulation) |  |  |  |  | 0 | [6 empty] | 0
| Supply and Application of external thermal insulation of ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg/CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. |  |  |  |  | 0 | [6 empty] | 0
a. | 25mm thick | SqM | RO | 805 | 230 | 1035 |  |  |  | RO | 805 | 230 | 1035
b. | 50mm thick | SqM | 80 | 1420 | 450 | 1870 | 113600 | 36000 | 149600 | 80 | 1300 | 400 | 1700 | 104000 | 32000 | 136000
2.7.2 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) - EXPOSED |  |  |  |  | 0 | [6 empty] | 0
| (Using Factory Laminated fibre glass insulation) |  |  |  |  | 0 | [6 empty] | 0
| Supply and Application of external thermal insulation of ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg/CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. Insulation shall be covered necessary glass cloth & UV protection paint. |  |  |  |  | 0 | [6 empty] | 0
a. | 25mm thick | SqM | RO | 1207.5 | 403 | 1610.5 |  |  |  | RO | 1207.5 | 403 | 1610.5
b. | 50mm thick | SqM | RO | 2358 | 633 | 2991 |  |  |  | RO | 2358 | 633 | 2991
[6 empty] | 0 | [6 empty] | 0
2.7.3 | THERMAL INSULATION FOR EXPOSED DUCTS-AIR WASHER DUCT |  |  |  |  | 0 | [6 empty] | 0
| Supply and Application of external thermal insulation of supply air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Quoted price shall be inclusive of adhesive, tapes as per specification. insulation shall be provided with necessary glass cloth & UV protection paint for ducts exposed to atmosphere as per specifications. |  |  |  |  | 0 | [6 empty] | 0
a. | 25 mm thick | Sqm | 35 | 1150 | 385 | 1535 | 40250 | 13475 | 53725 | 35 | 1095 | 385 | 1480 | 38325 | 13475 | 51800
a. | 19mm thick | SqM | RO | 1035 | 403 | 1438 |  |  |  | RO | 1035 | 382.85 | 1417.85
2.7.4 | THERMAL INSULATION FOR DUCTWORK-AIR WASHER DUCT IN AC AREA
Supply and Application of external thermal insulation of supply /return air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Quoted price shall be inclusive of adhesive, tapes as per specification. insulation shall be provided with aluminium foil, factory laminated.
a. | 25 mm thick | Sqm | 90 | 1150 | 385 | 1535 | 103500 | 34650 | 138150 | 90 | 1095 | 365 | 1460 | 98550 | 32850 | 131400
TOTAL ITEM NO. 2 (AIR DISTRIBUTION)
| TOTAL SUB-HEAD II carried over to Summary | [7 empty] | 3570952.5 | [6 empty] | 3063633.58