## MEP
PROJECT : AMD, CIP LOUNGE AT T1, AHEMDABAD AIRPORT
Date | October' 27, 2023
S.NO | ITEM DESCRIPTION | UNIT | QTY. | Rate (INR) | Amount (INR)
Part III | PLUMBING
A | SUB HEAD I-SANITARY FIXTURES AND FITTINGS
Note:
a) | All Sanitary fixtures including bottle traps (from approved make list), shall be issued free of cost by the "Employer". The contractor rates to include for supply all fixing/supporting accessories like nuts, bolts, screws, hangers, rubber buffers, CI or MS brackets, anchor fastners, sealents, washers, adhesives, Flanges, plumber's tape, white cement, masking tape (if required for protection), which are required for the successful installation of the fixtures/fittings in a neat workman like manner.
b) | Rates are inclusive of fixing/ work at all the heights, depths and locations within the project premises.
c) | Rates are inclusive of fixing/work for underslung plumbing system or embeded piping. Mostly, all the toilets in the residencial units have been designed for under slung piping.
d) | Provision of extension piece for final connection of CP fitting shall be supplied and installed by the contractor accordingly (as required)
e) | All pressure pipe will be tested on 1.5 times of there working pressure
1 | Providing, Supply, installation, testing and commisning of white vitreous china Wall mounted type "European" water closet pan with seat cover, closed coupled dual flush cistern (with all internal moving parts) with PVC heavy duty connectors, bolts, nuts, supporting arrangements, bakelite seat & cover with CP hinges & rubber buffers, P or S trap, connection to main pipe on shaft complete with all accessories including cutting & making good masonry holes/chasing in the walls & floors wherever required & health faucet with regulator with flexible pipe 1.5 m long, wall hooked complete as required, with all required accessories that includes Flush Plate ,bib cock made of CP brass complete as required. | No. | 0 | 24500 | 0
2 | Providing, Supply, installation, testing and commisning of white vitreous china "Floor mounted" type Composite Water closet (European type W.C. pan) with seat and lid, including with white Vitreous Chinaware matching Cistern complete with all accessories , also including with matching W.C. Pan with ISI marked white/Black solid plastic seat and Lid.Details of COST of one Pan composite with Cistern, Flush Pipe, EWC & Cistern complete with Fittings & Seat Cover,and one no. of Faucet for WB,with all required accessories that includes bib cock made of CP brass complete as required. (for Handicapped person's Toilet) | No. | 0 | 21500 | 0
3 | Providing and fixing white vitreous china rectangular Half pedestal Wash Basin & its accessories etc, also with all fittings and fixtures complete including cutting and making good the walls and floors wherever required. (for Handicapped person's Toilet) (colour- Star White) painted white, 32mm C.P. waste coupling, 32mm dia C.P. bottle trap and connection pipe upto wall with wall flange and rubber adopter for waste connection, complete including cutting and making good the walls, wherever required. | No. | 0 | 18500 | 0
4 | Providing, Supply, installation, testing and commisning of 15 mm dia C.P. brass basin mixer top mounted with C.P. wall flange of approved quality | No. | 0 | 2100 | 0
5 | Providing, Supply, installation, testing and commisning of CP Grab Bar swing type (in horizontal & vertical grabbing) & Grab rails 60 cm, complete including cutting and making good the walls, wherever required. | No. | 0 | 8500 | 0
6 | Providing, Supply, installation, testing and commisning of CP Grab rails 60 cm, complete including cutting and making good the walls, wherever required. | No. | 0 | 2000 | 0
7 | Providing, Supply, installation, testing and commisning of C.P. toilet paper holder with roller, with C.P brass screws, complete including cutting and making good the walls wherever required. | No. | 0 | 1750 | 0
8 | Providing, Supply, installation, testing and commisning of C.P. brass double towel rack 100mm wide and 600 long fixed with C.P. brass screws including cutting and making good the walls wherever required. | No. | 0 | 2500 | 0
9 | Providing, Supply, installation, testing and commisning of C.P twin Robt hook, fixed to wooden cleats with C.P. brass screws including cutting and making good the walls wherever required. | No. | 0 | 1250 | 0
10 | Providing, Supply, installation, testing and commisning of Twin manual 0.5 liter liquid soap dispenser with simple push lever fitted with liquid soap (one time),C.P. brass screws including cutting and making good the walls wherever required. | No. | 0 | 1850 | 0
11 | Providing, Supply, installation, testing and commisning of Automatic liquid soap dispenser with simple push lever fitted with liquid soap (one time),C.P. brass screws including cutting and making good the walls wherever required. | No. | 0 | 5500 | 0
12 | Providing, Supply, installation, testing and commisning of SS Baby Diaper changing station with all its accessories and components | No. | 0 | 35000 | 0
13 | Providing, Supply, installation, testing and commisning of SS 204 Grade Bin | No. | 0 | 2500 | 0
14 | Providing, Supply, installation, testing and commisning of C.P. Paper Towel Dispenser,with C.P brass screws, complete including cutting and making good the walls wherever required. | No. | 0 | 5000 | 0
15 | Providing and fixing white vitreous china rectangular wash basin under / over counter mounting, specially fabricated brackets to support the wash basin as per standard practice, painted white, 32mm C.P. waste coupling, 32mm dia C.P. bottle trap and connection pipe upto wall with wall flange and rubber adopter for waste connection, complete including cutting and making good the walls, wherever required. | No. | 0 | 17500 | 0
16 | Providing, Supply, installation, testing and commisning of Rain shower and total rain shower assembly including Concealed stop cock, long body bib cock & short body bib cock including wall chasing etc complete in toilet,with all required accessories for shower. | No. | 0 | 30500 | 0
17 | Providing, Supply, installation,testing and commissioning of Stainless steel shower drain channel 100 mm wide 800 mm length (max.) suitable to connect 50 mm drain outlet. | No | 0 | 8500 | 0
18 | Providing, fixing, testing and commissioning of white viterous china large flat back / half stall urinal supported by CI / MS bracket (duly painted with 2 coats of paints over a coat of primer), including CP brass waste with dome type grating, CP cast brass bottle trap with extension piece, wall flanges complete with all accessories & urinal partition with concealed CI bracket, cutting and making good, Including battery operated sensor based automatic flushing system for urinals, including sensor and required electrical and water connections etc, complete in all respect to make it fully functional including cutting and making good the walls etc. | No. | 0 | 35400 | 0
19 | Providing, Supply, installation, testing and commissioning of Stainless steel sink 304 Grade SS, Matt Finish medium size (220X440X200) supported by CI / MS Brackets duly painted, CP cast brass bottle trap with extension piece, rubber adaptor, CP copper connecting pipes, wall flange, union, CP brass chain, rubber plug, nuts, washers, waste connection complete & making good the walls, floor wherever required. | No. | 6 | 8845 | 53070
20 | Providing, Supply, installation, testing and commisning of 15 mm dia C.P. brass with dual lever faucet with C.P. wall flange of approved quality | No. | 6 | 1640 | 9840
21 | Providing, Supply, installation, testing and commisning of C.P. brass angle valve with C.P. wall flange, Nut and Washer etc. complete as required for 15 mm & 20 mm dia | No. | 12 | 1220 | 14640
22 | Providing, Supply, installation, testing and commisning of 15 mm dia C.P. brass bib cock with C.P. wall flange of approved quality | No. | 0 | 1185 | 0
23 | Providing, Supply, installation,testing and commissioning of Stainless steel sink (Single bowl with drainboard sink) 304 Grade SS,Matt Finish medium size 1000 X 500MM) supported by CI / MS Brackets duly painted, CP cast brass bottle trap with extension piece, rubber adaptor, CP copper connecting pipes, wall flange, union, CP brass chain, rubber plug, nuts, washers, waste connection complete & making good the walls, floor wherever required. | No. | 0 | 14500 | 0
24 | Providing, Supply, installation, testing and commisning of 15 mm dia C.P. brass sink mixer (wall mounted ) with 150 MM swivel spout, with C.P. wall flange of approved quality | No | 0 | 2650 | 0
25 | Providing, Supply, installation,testing and commissioning of High Speed hand dryer suitable to be operated with 230 volts, single phase, with fully hygienic operations with all accessories including cutting and making good the walls, wherever required. | No. | 0 | 20500 | 0
26 | Providing and fixing CP Brass 32mm size Bottle Trap of approved quality & make and as per the direction of Engineer-in-charge. | No. | 20 | 1170 | 23400
27 | Providing, Structural steel members in position at all levels and at all heights as specified in the drawings made out of standard MS sections consisting of MS angles, ISMC, ISMB conforming to local & international standards Cost to include fabricating necessary Gusset Plates, Stiffener plates, Brackets, Bolts, Cleats, seating angles etc., to the required size, shape, alignment etc, as per the drawings. Cost to include welding of members using structural steel welding electrodes as per ocal & international standards , necessary equipments, tools and tackles, staging, scaffolding required etc.,complete. including a coat of zinc chromate primer. | KG | RO | 750
28 | Providing, Supply, installation, testing and commisning of Grease Separator having grease storage capacity of 40 litre and total liquid holding capacity of 130 litre , all as per standard design and including making connections with sink. Material : Fabricated with 2 mm thick SS 304 grade stainless steel sheet | No. | 4 | 32200 | 128800
29 | Providing and fixing electric water storage heater (geyser) of following capacities including making inlet / outlet connections.
| a) Capacity : 35 litre | No. | 0 | 22500 | 0
| b) Capacity : 100 litre | No. | 0 | 45500 | 0
| c) Capacity : 125 litre | No. | 0 | 110000 | 0
| TOTAL SUB-HEAD I carried over to Summary |  |  |  | 229750
B | SUB HEAD II-WATER SUPPLY
30 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge.
Internal work - Exposed on wall
| 15 mm dia | RM | 150 | 485 | 72750
| 20 mm dia | RM | 80 | 570 | 45600
| 25 mm dia | RM | 35 | 710 | 24850
| 32 mm dia | RM | 35 | 880 | 30800
| 40 mm dia | RM | 21 | 975 | 20475
| 50 mm dia | RM | 19 | 1130 | 21470
| 65 mm dia | RM | 15 | 1260 | 18900
31 | Providing and fixing CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes with pipe as per CTS SDR 11 (operating pressure - 7 Bar @ 82 Deg C and 28 Bar @ 23 Deg C)for pipes from 1/2 Inch to 2 Inch. Schedule 40 Pipe to be used from 2-1/2 Inch to 6 Inch. Pipes shall be joined using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings (connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846. ASTM F441 with only CPVC solvent cement conforming to ASTM F-493.
Cost shall be inclusive of (a)Making maximum of 7.5 x 7.5 cm chasing in wall and floors for the pipe, making good the same by using 1:1 cement mortar over the wire mesh and providing protection to embedded pipes and fittings (in wall chase) by wrapping two layers of 400 micron polythene sheet including proper overlaps on joints complete as required or (b) Fixing/supporting the pipes (& fittings) at wall/ceiling level supported by galvanized clamps, hangers etc, as per specification. Exposed pipes to be painted of legends with direction arrow. GI pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealant compound at either end all as per Project Manager's / Consultant requirement. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings.
| 15 mm dia | RM | 250 | 545 | 136250
| 20 mm dia | RM | 20 | 588 | 11760
| 25 mm dia | RM | 15 | 755 | 11325
32 | Providing & fixing full way lever operated forged brass ball valve of brass body with forged brass hard chromeplated steel ball tested to a pressure not less than 15 Kg / sqcm with threaded / flanged joints complete with nuts, bolts, gaskets, washers etc.
| 20 mm dia | Nos. | 0 | 4670 | 0
| 25 mm dia | Nos. | 0 | 5150 | 0
| 32 mm dia | Nos. | 1 | 5790 | 5790
33 | Providing & fixing of butterfly valve (PN 16) with flanges, nut bolts, gaskets and necessary pad locking arrangement complete required.
| 65 mm dia | Nos. | 0 | 17500 | 0
34 | Supplying, laying/ fixing, testing and commissioning of following thickness resin bonded fiber glass pipe section insulation having density 80 kg/cum or mineral wool (non combustible) having density of 144 Kg/ cu m duly covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) on existing pipe and finally applying 0.63mm aluminium sheet cladding complete with type3 , grade 1 roofing feltstrip(as per IS:1322 as amended up to date ) at joints etc. as per specifications and as required.
| 25 mm thick mineral wool insulation (15 mm dia) | RM | 45 | 825 | 37125
| 25 mm thick mineral wool insulation (20 mm dia) | RM | 5 | 1215 | 6075
| 25 mm thick mineral wool insulation (25 mm dia) | RM | 0 | 1660 | 0
| 25 mm thick mineral wool insulation (32 mm dia) | RM | 0 | 2155 | 0
| TOTAL SUB-HEAD II carried over to Summary |  |  |  | 443170
C | SUB-HEAD III- DRAINAGE
35 | Providing, Supply, installation,testing and commissioning of UPVC Soil, Waste & Vent system conforming to IS : 13592 - Type B and UPVC fittings (moulded as well as fabricated) like bends, tees, Y-tees, crosses, boss connections, access pieces, saddle pieces, cleanouts, adaptors for connections to other materials, plugs, reducers, cowls, offSet and other specials. Jointing shall be done with pushfit EPDM ring jointing technique in general. Solvent cement joints may be provided for fittings and specials which are not manufactured with pushfit rubber joints. Pipes may be laid / fixed in sunken floors, under slung from ceiling. The pipes laid in sunken floor shall be encased with 75 mm thick cement concrete (1:2:4) all around. The installation shall be complete in all respects including cutting chases / holes in walls, slabs and making good the same as per specifications.
Providing GI pipe sleeves of suitable higher size wherever pipes crossing a fire rated wall / floor slab and sealing of space around pipe and pipe sleeve with glass wool in between and fire proof sealent at either end to the satisfaction of the Project Manager / Consultants and making good the same after pipes have been duly laid and testing complete.
| 110 mm dia | RM | 55 | 1098 | 60390
| 75 mm dia | RM | 60 | 965 | 57900
| 50 mm dia | RM | 4 | 800 | 3200
| 40 mm dia | RM | 80 | 671 | 53680
36 | Providing, fixing, jointing, testing and commissioning UPVC (Class III) Rain water downtake pipe conforming to IS:4985 cut to required lengths including all necessary fittings and specials.UPVC fittings (moulded as well as fabricated) like bends, tees, Y-tees, crosses, boss connections, access pieces, saddle pieces, cleanouts, adaptors for connections to other materials, plugs, reducers, cowls, offsets and other specials. Fixing at wall/ceiling level supported by galvanized steel clamps & hangers etc. Making proper connection with cement solvent joint as per BIS / manufacturer. Cutting, chases / holes in floors / walls / slab and making good wherever required. (All major MS structure to hold the stack with fixing including anchor fasteners,sand,cement etc is included in this item).
| 110 mm dia. | RM | 0 | 1850 | 0
37 | Providing and fixing of UPVC Floor Traps formed out of bore 'P' trap with 50 mm water seal, setting in 1:2:4 mix cement concrete block or clamping to the wall or suspending with the ceiling including cutting and making good the walls and floors wherever required, With Heavy class SS grating with Cockroach proof SS strainer of approved design including setting in floor with cement motor to match with floor finish as per architect requirement suitable for waster F.D. & F.T.
| 110 mm inlet and 75 mm outlet. | Nos. | 25 | 800 | 20000
38 | Providing and fixing of UPVC Urinal Traps formed out of bore 'P' trap with 50 mm water seal, setting in 1:2:4 mix cement concrete block or clamping to the wall or suspending with the ceiling including cutting and making good the walls and floors wherever required, With SS grating with Cockroach proof SS strainer of approved design including setting in floor with cement motor to match with floor finish as per architect requirement suitable for waster U.T.
| 110 mm inlet and 110 mm outlet. | Nos. | 0 | 1250 | 0
39 | Providing and fixing clean out/floor clean out plug consist of CI bend & GI socket heavy class with cap & key for opening male threaded cap etc. including lead caulked to CI pipes complete in all respects as per drawing/ sample approved by Engineer -in -Charge FCO (floor clean out plug shall be flushed with floor finish).: 100 mm dia. and Matching with Item no.31 or as per Architure approvals. | Nos. | 0 | 1500 | 0
40 | Providing and fixing floor drain made out of 110x75 mm OD uPVC. elbow connected to uPVC pipe complete as per direction of Project Manager. | Nos. | 0 | 850 | 0
41 | Making khurras 45x45 cm with average minimum thickness of 5 cm cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate of 20 mm nominal size) over P.V.C. sheet 1 m x1 m x 400 micron, finished with 12 mm cement plaster 1:3 (1 cement : 3 coarse sand) and a coat of neat cement, rounding the edges and making and finishing the outlet complete. | Nos. | RO | 60000
40 | Providing, jointing, testing and fixing UPVC Soil, Waste & Vent system conforming to IS : 13592 and UPVC fittings (moulded as well as fabricated) like bends, tees, Y-tees, crosses, boss connections, access pieces, saddle pieces, cleanouts, adaptors for connections to other materials, plugs, reducers, cowls, offset and other specials. Jointing shall be done with pushfit EPDM ring jointing technique in general. Solvent cement joints may be provided for fittings and specials which are not manufactured with pushfit rubber joints.
40.1 | 110 mm dia | RM | 25 | 1050 | 26250
0
41 | Providing and laying cement concrete 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40 mm nominal size) all-round sewerage pipes including bed concrete as per standard design : |  |  |  | 0
41.1 | 110 mm diameter | RM | 25 | 500 | 12500
42 | Providing and fixing square-mouth S.W. gully trap grade ‘A’' complete with C.I. grating, brick masonry chamber with water tight C.I. cover with frame of 300x300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design:
42.1 | 100x100 mm size P type
42.1.1 | With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | Each | 0 | 2450 | 0
43 | Providing, Supply, installation,testing and commissioning of Stainless steel drain over through grating channel 300 mm wide 600 mm length (max.) suitable to connect 50/75/110 mm drain outlet. | No | 0 | 4000 | 0
233920
TOTAL SUB-HEAD III carried over to Summary