## HVAC
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | FF46_IRISH HOUSE_HYDERABAD AIRPORT |  |  | DATE: | 2024-03-18
|  |  |  | REV: | R0
HVAC SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | HVAC SYSTEM EQUIPMENTS
KITCHEN EQUIPMENTS
A.1 | Supply, installation, testing, commissioning and field performance of ceiling suspended Electrostatic Precipitator (for removal of Kitchen Grease and Smoke particles) with all necessary supports and fittings. (Make: Rydair, Trion or equivalent with airport approval).
A.1.1 | 2500 CFM | Nos | 1
B | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
B.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
B.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 88
B.1.2 | 24 Gauge - (0.70 mm Thick) - Kitchen Supply Air Duct | Sq.Mtr | 58
B.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
B.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct | Sq.Mtr | 70
B.3 | Demolition of necessary Galvanized Iron (GI)/ Galvanized Steel (GS) ducts, as well as their closing and dummying to best align with the suggested HVAC system, are required. Contractor to conduct field verification and analysis based on site conditions.
B.3.1 | Supply Air Duct | LOT | 1
C | AIR DISTRIBUTION DUCT INSULATION & LINNING
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
C.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
C.1.1 | 19 mm thicknesses - (SAD) - External Duct Insulation | Sq.Mtr | 88
C.1.2 | 19 mm thicknesses - (KSAD) - External Duct Insulation | Sq.Mtr | 58
C.2 | Supply, installation & testing of Thermal Insulation of ducting using glass wool with silver foil covering, density 40 Kg/m3, Thermal Conductivity λ - 0.030 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
C.2.1 | 80 mm thicknesses - (KEAD) - External Duct Insulation | Sq.Mtr | 70
D | AIR DISTRIBUTION DUCT ACCESSORIES
DUCT AIR CONTROL DAMPERS
D.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
D.1.1 | Size - 900 x 350 mm | Nos | 1
D.1.2 | Size - 600 x 200 mm | Nos | 1
D.1.3 | Size - 400 x 150 mm | Nos | 1
D.1.4 | Size - 300 x 350 mm | Nos | 1
D.1.5 | Size - 750 x 300 mm | Nos | 1
D.1.6 | Size - 700 x 250 mm | Nos | 1
D.1.7 | Size - 900 x 350 mm MS FLANGE | Nos | 1
D.1.8 | Size - 700 x 250 mm MS FLANGE | Nos | 1
D.1.9 | Size - 350 x 150 mm MS FLANGE | Nos | 1
D.1.10 | Size - 550 x 250 mm MS FLANGE | Nos | 1
E | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Single Deflection Grille with opposed blade collar damper aerofoil adjustable front and rear blades with collar damper frame of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.1.1 | Neck Size - 750 x 150 mm | Nos | 9
E.1.2 | Neck Size - 750 x 150 mm - without damper | Nos | 9
E.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Double Deflection Grille with opposed blade collar damper aerofoil adjustable blades with of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.2.1 | Neck Size - 350 x 350 mm | Nos | 8
E.2.2 | Neck Size - 350 x 350 mm - without damper | Nos | 4
F | TESTING & COMMISIONING
F.1 | Duct Air Balancing & Commisioning | Lot | 1
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.