## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
B | AIR DISTRIBUTION DUCTS RECTANGULAR DUCTS
B.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
B.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 88
B.1.2 | 24 Gauge - (0.70 mm Thick) - Kitchen Supply Air Duct | Sq.Mtr | 58
B.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
B.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct | Sq.Mtr | 70
B.3 | Demolition of necessary Galvanized Iron (GI)/ Galvanized Steel (GS) ducts, as well as their closing and dummying to best align with the suggested HVAC system, are required. Contractor to conduct field verification and analysis based on site conditions.
B.3.1 | Supply Air Duct | LOT | 1
C | AIR DISTRIBUTION DUCT INSULATION & LINNING AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
C.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
C.1.1 | 19 mm thicknesses - (SAD) - External Duct Insulation | Sq.Mtr | 88
C.1.2 | 19 mm thicknesses - (KSAD) - External Duct Insulation | Sq.Mtr | 58
C.2 | Supply, installation & testing of Thermal Insulation of ducting using glass wool with silver foil covering, density 40 Kg/m3, Thermal Conductivity λ - 0.030 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
C.2.1 | 80 mm thicknesses - (KEAD) - External Duct Insulation | Sq.Mtr | 70
D | AIR DISTRIBUTION DUCT ACCESSORIES DUCT AIR CONTROL DAMPERS
D.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
D.1.1 | Size - 900 x 350 mm | Nos | 1
D.1.2 | Size - 600 x 200 mm | Nos | 1
D.1.3 | Size - 400 x 150 mm | Nos | 1
D.1.4 | Size - 300 x 350 mm | Nos | 1
D.1.5 | Size - 750 x 300 mm | Nos | 1
D.1.6 | Size - 700 x 250 mm | Nos | 1
D.1.7 | Size - 900 x 350 mm MS FLANGE | Nos | 1
D.1.8 | Size - 700 x 250 mm MS FLANGE | Nos | 1
D.1.9 | Size - 350 x 150 mm MS FLANGE | Nos | 1
D.1.10 | Size - 550 x 250 mm MS FLANGE | Nos | 1
E | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS) GRILLES
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Single Deflection Grille with opposed blade collar damper aerofoil adjustable front and rear blades with collar damper frame of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.1.1 | Neck Size - 750 x 150 mm | Nos | 9
E.1.2 | Neck Size - 750 x 150 mm - without damper | Nos | 9
E.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Double Deflection Grille with opposed blade collar damper aerofoil adjustable blades with of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.2.1 | Neck Size - 350 x 350 mm | Nos | 8
E.2.2 | Neck Size - 350 x 350 mm - without damper | Nos | 4
F | TESTING & COMMISIONING
F.1 | Duct Air Balancing & Commisioning | Lot | 1