## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
A | DRAINAGE SYSTEM
INTERCEPTORS & SEPERATORS
A.1 | Supplying, Installing, Testing & Commissioning of Greese Trap or Grease Interceptor (Above Ground / floor) of 304 grade stainless steel material with interceptor body, preforated bucket, baffles, integral trap, inlet & outlep pipe sleeve and stainless steel interceptor cover of approved make and with all necessary fittings & connectors etc. (Make : Nugreen , Kessel and Concessionaire can propose another make in SS material.)
A.1.1 | NGT 50 - Flow Rate (1.58 LPS / 95 LPM) | Nos | 1
VALVES & ACCESSORIES
A.2 | Supplying, Installing, Testing & Commissioning of ABS Air Admittance Valve conforming to EN 12380, with an air admittance air flow rate of 6.1 L/s and a temperature range of operation from -20 C to + 60 C of approved make with all necessary adapters, fittings and connectors etc. (Make : Astral/Supreme for Pipe and Fittings)
A.2.1 | 32 mm Dia | Nos | 1
DRAINS, TRAPS & CLEANOUTS
A.3 | Supplying, Installing, and testing of Inspection Chamber with cast iron air tight cover plate with all necessary civil water proofing, gas tight rubber seal, perforated mesh, pipe inlet & outlet connections etc. construction details as advised by Airport authorities.
A.3.1 | 600 mm X 600 mm | Nos | 1
A.4 | Supplying, Installing, and testing of AISI 304 grade Stainless Steel Trench Channel Floor Drain with top square anti-slip mesh grating drain cover of 300 X 300 mm, lateral/horizontal outlet, with removable waste basket, odor water seal trap of approved make with all necessary adapters, fittings, and connectors etc. (Make : Custom made)
A.4.1 | 50 mm Dia - Outlet | Nos | 7
A.5 | Supplying, Installing & Testing of cast iron Floor Trap (150 mmx 150 mm) with Stainless Steel slotted top cover, odour water seal trap of approved make with all necessary adapters, fittings and connectors etc. (Makes : NECO or equivalent with Airport approval)
A.5.1 | 75 mm Dia - Outlet | Nos | 2
A.6 | DRAINAGE SYSTEMS PIPING Supplying, Installing, Testing, and Commissioning of uPVC Pipe, for drainage with all necessary fittings such as bends, wye's, reducers, san tee's, double wye's, double combinations, san cross, and cleanout plugs etc, of approved make. and with all necessary supports/clamps for the above-raised floor pipes as per standards and site conditions/requirements. (Make : Astral/Supreme for Pipe and Fittings)
A.6.1 | 32 mm Dia | Mtr | 1
A.6.2 | 40 mm Dia | Mtr | 8
A.6.3 | 50 mm Dia | Mtr | 27
A.6.4 | 75 mm Dia | Mtr | 5
B | WATER SUPPLY SYSTEM
WATER SUPPLY EQUIPMENTS
B.1 | Supply, Installation, Testing & Commissioning of Electric Water Heater with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. and proper supports necessary as per standards and site condition / requirements. (Make : Crompton/Bajaj or equivalent with Airport approval)
B.1.1 | 40 Liters vertical storage water heater | Nos | 1
B.1.2 | 30 Liters vertical storage water heater | Nos | 1
B.2 | Supply, Installation, Testing & Commissioning of RO Filteration Unit for supplying pure filtered potable water to equipments like Combi-steamers & baking ovens, Fresh water taps & Coolers, Coffee/ Espresso machines, Dish-washers, Post-mix machines, Ice-machines, and Boiling-water taps etc. with necessary prefilters, filter cartridges, manifold heads, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. Final make, model and details to be finalized by specialist vendor after examining the water test report of incoming water supply provided at site. (Make : Eco Smart/Aquaguard or equivalent with Airport approval)
B.2.1 | 15 Ltrs / Hr - Flow Rate | Nos | 3
WATER SUPPLY PIPE VALVES & ACCESSORIES
B.3 | Supply, Installation, Testing & Commissioning of Brass Ball Valve with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar of approved make and with all necessary fittings. (Makes : NECO or equivalent with Airport approval)
B.3.1 | 15 mm Dia | Nos | 6
B.4 | Supply, Installation, Testing, and Commissioning of chrome plated Angle Valve with wall flange/rosette for all plumbing equipment/fixtures with a pressure rating of 16 Bar of approved make and with all necessary fittings. Including making good the wall/partition as per Architectural / Interior Design and as per relevant standards. (Makes : NECO or equivalent with Airport approval)
B.4.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 23
COLD WATER SUPPLY PIPING
B.5 | Supply, Installation, Testing & Commissioning of (Chlorinated Poly Vinyl Chloride) CPVC Pipe conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Astral/Supreme for Pipe and Fittings)
B.5.1 | 15 mm Dia | Mtr | 9
B.5.2 | 20 mm Dia | Mtr | 32
B.5.3 | 25 mm Dia | Mtr | 12
B.6 | Supply, Installation, Testing & Commissioning of Copper Pipe conforming to BS 2871 / EN 1057, (continous operating temperature range of maximum 90°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Manibhadra fittings or equivalent with Airport approval)
B.6.1 | 15 mm Dia | Mtr | 21
PIPING THERMAL INSULATION
B.7 | Supply & fixing of Pipe Insulation of 13 mm thick, with Polyethylene-based, closed-cell foam pipe insulation and polymer protective coating to prevent external mechanical damage of approved make for Hot water pipe with a operating temperature range of 0°C to 100°C, Thermal conductivity (λ) 0.038 W/m-K @ 40°C including suitable adhesives to fix the insulation to pipe. (Make : Thermax, Maxima, Fuelpac or equivalent)
B.7.1 | 15 mm Dia | Mtr | 21