## PHE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | FF-025_MILLIE COOKIES_HYDERABAD AIRPORT |  |  | DATE: | 2024-02-27
|  |  |  | REV: | R0
PLUMBING SYSTEM - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | DRAINAGE SYSTEM
INTERCEPTORS & SEPERATORS
A.1 | Supplying, Installing, Testing & Commissioning of Greese Trap or Grease Interceptor (Above Ground / floor) of 304 grade stainless steel material with interceptor body, preforated bucket, baffles, integral trap, inlet & outlep pipe sleeve and stainless steel interceptor cover of approved make and with all necessary fittings & connectors etc. (Make : Nugreen , Kessel and Concessionaire can propose another make in SS material.)
A.1.1 | NGT 14 - Flow Rate (0.46 LPS / 28 LPM) | Nos | 1
VALVES & ACCESSORIES
A.2 | Supplying, Installing, Testing & Commissioning of ABS Air Admittance Valve conforming to EN 12380, with an air admittance air flow rate of 6.1 L/s and a temperature range of operation from -20 C to + 60 C of approved make with all necessary adapters, fittings and connectors etc. (Make : Astral/Supreme for Pipe and Fittings)
A.2.1 | 32 mm Dia | Nos | 1
DRAINS, TRAPS & CLEANOUTS
A.3 | Supplying, Installing, and testing of AISI 304 grade Stainless Steel Floor Drain with top square anti-slip mesh grating drain cover of 300 X 300 mm, lateral/horizontal outlet, with removable waste basket, odor water seal trap of approved make with all necessary adapters, fittings, and connectors etc. (Make : Custom made)
A.3.1 | 50 mm Dia - Outlet | Nos | 1
A.4 | Supplying, Installing & Testing of cast iron Floor Trap (150 mmx 150 mm) with Stainless Steel slotted top cover, odour water seal trap of approved make with all necessary adapters, fittings and connectors etc. (Makes : NECO or equivalent with Airport approval)
A.4.1 | 75 mm Dia - Outlet | Nos | 1
DRAINAGE SYSTEMS PIPING
A.5 | Supplying, Installing, Testing, and Commissioning of uPVC Pipe, for drainage with all necessary fittings such as bends, wye's, reducers, san tee's, double wye's, double combinations, san cross, and cleanout plugs etc, of approved make. and with all necessary supports/clamps for the above-raised floor pipes as per standards and site conditions/requirements. (Make : Astral/Supreme for Pipe and Fittings)
A.5.1 | 32 mm Dia | Mtr | 2
A.5.2 | 40 mm Dia | Mtr | 5
A.5.3 | 50 mm Dia | Mtr | 10
A.5.4 | 75 mm Dia | Mtr | 5
B | WATER SUPPLY SYSTEM
WATER SUPPLY EQUIPMENTS
B.1 | Supply, Installation, Testing & Commissioning of Electric Water Heater with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. and proper supports necessary as per standards and site condition / requirements. (Make : Crompton/Bajaj or equivalent with Airport approval)
B.1.1 | 15 Liters vertical storage water heater | Nos | 1
B.2 | Supply, Installation, Testing & Commissioning of RO Filteration Unit for supplying pure filtered potable water to equipments like Combi-steamers & baking ovens, Fresh water taps & Coolers, Coffee/ Espresso machines, Dish-washers, Post-mix machines, Ice-machines, and Boiling-water taps etc. with necessary prefilters, filter cartridges, manifold heads, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. Final make, model and details to be finalized by specialist vendor after examining the water test report of incoming water supply provided at site. (Make : Eco Smart/Aquaguard or equivalent with Airport approval)
B.2.1 | 15 Ltrs / Hr - Flow Rate | Nos | 1
WATER SUPPLY PIPE VALVES & ACCESSORIES
B.3 | Supply, Installation, Testing & Commissioning of Brass Ball Valve with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar of approved make and with all necessary fittings. (Makes : NECO or equivalent with Airport approval)
B.3.1 | 15 mm Dia | Nos | 4
B.4 | Supply, Installation, Testing, and Commissioning of chrome plated Angle Valve with wall flange/rosette for all plumbing equipment/fixtures with a pressure rating of 16 Bar of approved make and with all necessary fittings. Including making good the wall/partition as per Architectural / Interior Design and as per relevant standards. (Makes : NECO or equivalent with Airport approval)
B.4.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 4
COLD WATER SUPPLY PIPING
B.5 | Supply, Installation, Testing & Commissioning of (Chlorinated Poly Vinyl Chloride) CPVC Pipe conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Astral/Supreme for Pipe and Fittings)
B.5.1 | 15 mm Dia | Mtr | 10
B.5.2 | 20 mm Dia | Mtr | 10
B.5.3 | 25 mm Dia | Mtr | 3
B.6 | Supply, Installation, Testing & Commissioning of Copper Pipe conforming to BS 2871 / EN 1057, (continous operating temperature range of maximum 90°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Manibhadra fittings or equivalent with Airport approval)
B.6.1 | 15 mm Dia | Mtr | 4
PIPING THERMAL INSULATION
B.7 | Supply & fixing of Pipe Insulation of 13 mm thick, with Polyethylene-based, closed-cell foam pipe insulation and polymer protective coating to prevent external mechanical damage of approved make for Hot water pipe with a operating temperature range of 0°C to 100°C, Thermal conductivity (λ) 0.038 W/m-K @ 40°C including suitable adhesives to fix the insulation to pipe. (Make : Thermax, Maxima, Fuelpac or equivalent)
B.7.1 | 15 mm Dia | Mtr | 4
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.