## Summary
S.NO | Outlet | TFS Amount
1 | Bun Extra Work | 58284.112
2 | Shop 1 Extra Work | 85034.016
3 | Shop 2 Extra Work | 84951.12
4 | Rates for Bun Tea & Other Shop- Extra Work | 3760
TOTAL WITHOUT GST |  | 232029.248

## Bun Tea
Sr No | Item of description | Unit | No | L | W | Total | TFS Rates | TFS Amount
1 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 / 1239 for hydrent and sprinkler applications including fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, U bolt and including painting of two coats of Red Oxide , painting with two or more coats of synthetic enamel paint of Post office red shade complete as required.The installation includes all civil openings , breakages and making good the same. ( Final Quantity Measure as per site after working ) | [6 empty] | 0
| 25mm | rmt | 1 | 4 |  | 4 | 430 | 1720
0
2 | Supplying, installation, testing & commissioning of sprinkler 1500mm length flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required. | nos |  |  |  | 2 | 1350 | 2700
0
0
4 | Supplying and erecting PVC armoured cable 2 core 1.5 sq. mm FRLS copper conductor complete erected on wall / celling as per specification | rmt |  |  |  | 110 | 140 | 15400
| MCP to smoke (3+3.4+.6+dropper 8) |  | 1 | 15 |  | 15 |  | 0
| Hooter (1+1+3.4+.6) |  | 1 | 6 |  | 6 |  | 0
| Main zone ro hooter (1.5+3+5+5+5+5+7+5+4+2+2)*2 |  | 1 | 89 |  | 89 |  | 0
0
5 | P/L PVC pipe with chasing of wall | nos |  |  |  | 2 | 200 | 400
0
6 | Supply and laying, effecting proper connections, testing & commissionin of 1.1 KV 4C x 16 Sq.mm. XLPE FRLS armoured cable. | rmt |  |  |  | 70 | 300 | 21000
0
7 | Providing and laying a proprietary chemical waterproofing system consisting of polymer-modified acrylic base coating in two coats in the form of a slurry (total consumption of 1.5 Kg/Sqm) as approved by the PM and as directed by the approved manufacturer of waterproofing coating, with sandwiched fiber mesh and protective screed. The work shall include cleaning the surface, grouting porous surfaces making ‘V’ grooves at junctions, cracks with nonshrink crystalline base cementitious grout, etc. Further including horizontal and vertical surfaces protected with 20mm screeding in 1:4 mortar (1 cement: 4 sand), finished in ready to receive Architectural finish, in the correct line, level, and plumb, curing, grouting, testing, etc. all complete to the entire satisfaction of the PM. | sft |  |  |  | 198.3014 | 80 | 15864.112
| BUN TEA TOTAL AREAR |  | 1 | 18.58 | 7.83 | 145.4814 |  | 0
| LHS & RHA WALL |  | 2 | 1 | 7.83 | 15.66 |  | 0
| FRONT AND BACK WALL |  | 2 | 1 | 18.58 | 37.16 |  | 0
0
8 | Making core cuts of 110mm dia for main drain tap off | nos | 1 |  |  | 1 | 1200 | 1200
0
Grand Total | [7 empty] | 58284.112
NOTE: | Rate analysis is required for final bill closure according to market standards. For the items rate not included in our BOQ, we requried detailed Rates Breakup with market rates standard for final approval.

## Sub way shop no 1
Sr No | Item of description | Unit | No | L | W | Total | TFS Rates | TFS Amount
1 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 / 1239 for hydrent and sprinkler applications including fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, U bolt and including painting of two coats of Red Oxide , painting with two or more coats of synthetic enamel paint of Post office red shade complete as required.The installation includes all civil openings , breakages and making good the same. ( Final Quantity Measure as per site after working ) | [6 empty] | 0
| 40mm | RMT | 1 | 7 |  | 7 | 710 | 4970
0
0
3 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required. |  |  |  |  | 3 | 1350 | 4050
| 1500mm long flexiblwe sprinkler pipe | RMT |  |  |  | 3 |  | 0
0
0
2 | Supplying and erecting PVC armoured cable 2 core 1.5 sq. mm FRLS copper conductor complete erected on wall / celling as per specification |  |  |  |  | 127.9 | 140 | 17906
| Sub way shop 1 (3.4+4+5+1.1+5+2.5+5+5+4.9+2.5+.7+1.5)*2 | RMT | 1 | 91.2 |  | 91.2 |  | 0
| HOOTER DROP |  | 3 | 4 |  | 12 |  | 0
| Shop no 1(5+1+1.1+beam.6+point drop 8+MCP drop 6+hooter 3) |  | 1 | 24.7 |  | 24.7 |  | 0
0
5 | P/L PVC pipe with chasing of wall | RMT |  |  |  | 2 | 200 | 400
0
0
6 | Supply and laying, effecting proper connections, testing & commissionin of 1.1 KV 4C x 16 Sq.mm. XLPE FRLS armoured cable. | RMT |  |  |  | 115 | 300 | 34500
0
7 | Making core cuts of 110mm dia for main drain tap off | NOS | 1 |  |  | 1 | 1000 | 1000
0
7 | Providing and laying a proprietary chemical waterproofing system consisting of polymer-modified acrylic base coating in two coats in the form of a slurry (total consumption of 1.5 Kg/Sqm) as approved by the PM and as directed by the approved manufacturer of waterproofing coating, with sandwiched fiber mesh and protective screed. The work shall include cleaning the surface, grouting porous surfaces making ‘V’ grooves at junctions, cracks with nonshrink crystalline base cementitious grout, etc. Further including horizontal and vertical surfaces protected with 20mm screeding in 1:4 mortar (1 cement: 4 sand), finished in ready to receive Architectural finish, in the correct line, level, and plumb, curing, grouting, testing, etc. all complete to the entire satisfaction of the PM. | SQFT |  |  |  | 277.6002 | 80 | 22208.016
| SHOP -1 TOTAL AREAR | 1 | 26.33 | 7.94 |  | 209.0602 |  | 0
| LHS & RHA WALL | 2 | 26.33 | 1 |  | 52.66 |  | 0
| FRONT AND BACK WALL | 2 | 7.94 | 1 |  | 15.88 |  | 0
[6 empty] | Grand Total |  | 85034.016
NOTE: | Rate analysis is required for final bill closure according to market standards. For the items rate not included in our BOQ, we requried detailed Rates Breakup with market rates standard for final approval.

## Sub way shop no 2
Sr No | Item of description | Unit | No | L | W | Total | TFS Rates | Material Rate | Labour Rate | Wastage | Rupess | Remark's | TFS Amount
1 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 / 1239 for hydrent and sprinkler applications including fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, U bolt and including painting of two coats of Red Oxide , painting with two or more coats of synthetic enamel paint of Post office red shade complete as required.The installation includes all civil openings , breakages and making good the same. ( Final Quantity Measure as per site after working ) | [11 empty] | 0
| 40mm |  | 1 | 7 |  | 7 | 710 | [5 empty] | 4970
| 25mm (1.8+1.8+1.8) |  | 1 | 5.4 |  | 5.4 | 430 | [5 empty] | 2322
0
2 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required. |  |  |  |  | 3 | 1350 | [5 empty] | 4050
| 1500mm long flexiblwe sprinkler pipe |  |  |  |  | 3 | [6 empty] | 0 | OK
0
0
0
4 | Supplying and erecting PVC armoured cable 2 core 1.5 sq. mm FRLS copper conductor complete erected on wall / celling as per specification |  |  |  |  | 117.2 | 140 | [5 empty] | 16408
| Sub way shop 2 (3.4+4+5+1.1+5+2.5+5+5+5+4.9+2.5+.7+1.5)*3 |  | 1 | 91.2 |  | 91.2 | [6 empty] | 0 | OK
| Shop no 2 (MCP (2.7+2.7+2+2+4+.6+9) |  | 1 | 23 |  | 23 | [6 empty] | 0 | OK
| Hooter (3) |  | 1 | 3 |  | 3 | [6 empty] | 0 | OK
0
5 | P/L PVC pipe with chasing of wall |  |  |  |  | 2 | 200 | [5 empty] | 400 | OK
0
0
6 | Supply and laying, effecting proper connections, testing & commissionin of 1.1 KV 4C x 16 Sq.mm. XLPE FRLS armoured cable. | RMT |  |  |  | 120 | 300 | [5 empty] | 36000 | ZONE WISE JMS DETAILS REQUIRED | Rate analysis
0
7 | Making core cuts of 110mm dia for main drain tap off | nos | 1 |  |  | 1 | 1000 | [5 empty] | 1000 | OK
0
7 | Providing and laying a proprietary chemical waterproofing system consisting of polymer-modified acrylic base coating in two coats in the form of a slurry (total consumption of 1.5 Kg/Sqm) as approved by the PM and as directed by the approved manufacturer of waterproofing coating, with sandwiched fiber mesh and protective screed. The work shall include cleaning the surface, grouting porous surfaces making ‘V’ grooves at junctions, cracks with nonshrink crystalline base cementitious grout, etc. Further including horizontal and vertical surfaces protected with 20mm screeding in 1:4 mortar (1 cement: 4 sand), finished in ready to receive Architectural finish, in the correct line, level, and plumb, curing, grouting, testing, etc. all complete to the entire satisfaction of the PM. | sft |  |  |  | 247.514 | 80 | [5 empty] | 19801.12 |  | Bikanerwala rates
| SHOP -2 TOTAL AREAR |  | 1 | 26.26 | 6.9 | 181.194 | [6 empty] | 0 | OK
| LHS & RHA WALL |  | 2 | 26.26 | 1 | 52.52 | [6 empty] | 0 | OK
| FRONT AND BACK WALL |  | 2 | 6.9 | 1 | 13.8 | [6 empty] | 0 | OK
| TOTAL | [11 empty] | 84951.12
NOTE: | Rate analysis is required for final bill closure according to market standards. For the items rate not included in our BOQ, we requried detailed Rates Breakup with market rates standard for final approval.

## Rate analysis (hidden)
Sr No | Item |  |  | QTY | RATE | UNIT | COST
2 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required.
| 1.5 mtr. Long corrogated stainless steel flexible Avg. basic rate |  |  | 1 | 630 | No. | 630
| Accessories (Fttings) |  |  | 1 | 300 | LS | 300
| Resette Plate |  |  | 1 | 40 | No. | 40
| Spenkler Pendent type 15 mm dia |  |  | 1 | 220 | No. | 220
| welding Rod |  |  | 3 | 3.95 | No. | 11.85
| The material cost = | [5 empty] | 1201.85
| Add 5% wastage(s.no 2&3)= | [5 empty] | 0
| Total material cost = | [5 empty] | 1201.85
| Scaffolding |  |  | 1 | 100 | LS | 100
| Tools & Plants @ 1.5% | [5 empty] | 18.0277
| Transportation Cost @ 5% | [5 empty] | 60.0925
| Total material cost = | [5 empty] | 1379.9702
| Labour cost = | [5 empty] | 800
| cost of 1.5 mtr. Long corrogated stainless steel ( grade AISI 304 ) flexible = | [5 empty] | 2179.9702
| 20% contractor profit = | [5 empty] | 435.9941
| The total cost of 1.5 mtr. Long corrogated stainless steel ( grade AISI 304 ) flexible = |  |  |  |  | Nos | 2615.9643
| Description | Base Rate | Unit | 3% Wastage | Hardware/Fitting | Labour Charges | 2% Tools & Plants | 1% Transport Charges | Amount | 20% O/H & profit | Total Amount
6 | 4C x 16 Sq.mm. XLPE FRLS armoured cable. | 240 | Mtr | 7.2 | 10 | 35 | 4.8 | 2.4 | 299.4 | 59.88 | 359.28

## Rate Agreed
Sr No | Item of description | Unit | No | L | W | Total | TFS Rates | Material Rate | Labour Rate | Wastage | Rupess | Remark's | TFS Amount
3 | P/F Sprinkler Pendent | nos |  |  |  | 2 | 470 | [5 empty] | 940
4 | P/F Sprinler Pendent | NOS |  |  |  | 3 | 470 | [5 empty] | 1410
3 | P/F Sprinler Upright |  |  |  |  | 3 | 470 | [5 empty] | 1410
Total Amount | [12 empty] | 3760