## Summary
Sr No | Particulars | AS PER TFS ANNEXURE AMOUNT-1
1 | Interior Works | 99774.9
2 | Plumbing Works | 30557.4
3 | Interiror Electrical | 72350
4 | Fire Fighting | 4660
TOTAL |  | 207342.3
Note on C4: AMOUNT CORRECTED WITH AUTO-SUM IN ELECTRICAL WORK BOQ ITEM.
Note on C5: AMOUNT CORRECTED WITH FIRE-PENDANT QTY.

## GIANI CIVIL&INTERIOR BOQ
Una-Foodcourt-Gianis
2024-01-09
BOQ STANDARDISATION, IMPLEMENTATION AND COST CONSULTANCY
GENERAL NOTES
Please refer to "Exhibit A - Basic rate of material" for the applicable base rates of materials
Items of works shall to be read in conjunction with Drawings, Specifications, Contractual terms and conditions and Trade Preambles to this BOQ as included in the RFP.
The quantities mentioned in the BOQ is tentative and may increase or decrease. Payment shall be restricted to the quantum of work executed and measured as per the defined mode of measurement.
The Mode of Measurement (in order of priority) is as follows:
(i) As defined in relevant item in the BOQ
(ii) As defined in the specification
(iii) As defined in IS-1200 or (latest version) for relevant trade .
(iv) if mode is not defined in (i), (ii) and (iii), the standard industry practice shall be adopted.
Items of work and trade preambles are essential parts of the bill of quantities and are to be taken as mutually explanatory of one another. Requirement occurring in one is binding as though occurring in both. In resolving conflicts, discrepancies, errors or omissions as regards trade preambles & bill of quantities the following order of precedence shall be used but subject to PRIORITY OF DOCUMENTS as included in General Conditions of Contract: a. General Notes as included in this bill of quantities.
SR.NO. | ITEM | DESCRIPTION | UNIT | EXECUTED QTY | ANNEXURE RATE | ANNEXURE AMOUNT
1 | Kitchen equipments unloading/ shifting | Unloading/Shifitng/ fixing of kitchen equipments. | JOB |  | 0 | 0
Civil works
2 | Internal Plaster | P&A of single coat backing plaster of 15-18 mm thick in CM 1:4 proportion to the walls & others surface including scaffolding, curing the joints, etc. The rates are inclusive of providing chicken mesh of 18mm gauge & 150mm width at junction of brick & RCC etc. at the walls, columns, beams etc., seven days water treatment as anti crack of plaster. Complete as per site engineer's instruction. | Sq.Ft |  | 0 | 0
3 | Half brick partition walls | Providing and laying 4 1/2" thick half brickwork in partition walls and architectural elements etc., with well burnt 1st class table moulded, good quality approved bricks in 1:4 Cement Mortar (1 Cement : 4 Coarse Sand by volume) including soaking the bricks in water adequately and drying, scaffolding, curing, rubbing the surface, raking out the joints etc., complete as directed and specified. | Sq.Ft | 4.575 | 110 | 503.25
4 | PCC Work | Providing and laying up to 50-75 mm thick cement concrete flooring with 1:2:4 cement concrete laid to proper level and slope in alternate bays including compactions, filling joints, or as directed, finishing smooth with cement Mortar 1:1 of sufficient minimum thickness to give a smooth & even surface and curing etc. complete as per architects instructions. | Sq.Ft | 140.04 | 60 | 8402.4
5 | COBA Work | CINDER BLOCK COBA of Avg. thickness mentioned below; After laying of soil pipes, floor traps is completed the floor of the sunken portion shall be covered with cinder coba embedded manually with 15-20 mm wide joints in 20 mm thk. Waterproofing mortar 1:4 ( 1 cement : 4 coarse sand )in layers upto the full ht. of sunken portion, having top layer of 50 mm thk waterproof mortar 1:4 ( 1 cement : 4 coarse sand ) using specialized W.P. chemical, finished smooth / rough with floating coat of neat cement all complete and as per specification. | Sq.Ft | 140.04 | 90 | 12603.6
6 | Kota Skirting | Fixing & laying of 150mm high kota stone for skirting with bedding of appropriate approved make adhesive & colour joint filler inclusive of making all groove/chamfering/rounding/hole where ever required, in proper line and level in all direction, polishing/finishing/cleaning etc. Complete as per detail drawing, specification and as directed by PMC. | RFT | 41 | 100 | 4100
8 | SS Corner Guard | P&F of 304 grade 3mm thick SS Corner guard (30mm x 30mm), finished as per approved sample fixing with SS full thread screws on each corner of the kitchen's wall before cladding of tiles, so that the corner may be protected from damage. Complete in proper line &level and site engineer's instruction. | RFT |  | 0 | 0
Flooring & Cladding
11 | Kota Flooring | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : | SFT | 144.29 | 145 | 20922.05
14 | Subway Wall Tile Cladding -2 | Providing and fixing in subway tile of approved make & shade on any surface as per details in drawing and Over 12 mm thk bed of cement mortar 1:3 (cement: fine sand ) with thick grey cement slurry, with hairline joints using cement grout. The job includes cutting tiles & making smooth edges wherever required. The work shall also include the cost of materials, wastages, labor, all lead and lift at all levels, loading and unloading, transportation, curing, etc., and all other incidental charges, etc. Complete as specified in the drawing & to the satisfaction of the Site Engineer. Ceramic wall tile (Printed) With customized line work Make: -Johnson in exposed area / Ceramic wall tile white/ Satin white 75x300mm below the counter or hidden area | SFT | 136.9 | 165 | 22588.5
16 | Wall Textured Paint | Providing & applying two or more coats of Textured paint/surface coating of approved make and shade over walls etc. after preparing the surface with a coat of primer and 4-6mm thick plaster of Paris punning to give a smooth and even surface etc. | SFT |  | 0 | 0
17 | Wooden beading work | Providing and fixing solid teak wood fixed on wall. Size: 50 x 18mm as per detail drawing. Finished with clear Melamine Polish in matte finish. | RFT |  |  | 0
Ceiling
18 | Gypsum false ceiling (MOH area) | Gypsum Board false Ceiling: Providing, fabrication and fixing in position of false ceiling ( height will be decided on the spot as per site conditions) by fixing 12 mm Th. Gypsum Board sheets on frame work of GI sheet section. The main runners of 22 gauge GI sheet and cross runners of 24 gauge GI sheet must be framed to form a mesh of 2’0”x2’0” c/c. The Gypsum Board must be fixed to the GI frame and joint to be properly filled in with POP paste and paper tape to get a leveled smooth ceiling. Recessing of the Gypsum Board for light fixtures must be done along with extra frame work of GI sheet section to hold the concealed light fixtures etc. directed by the site engineer. Including two coats of primer suitable for gypsum board two or more coats of plastic emulsion paint of approved shade and also including making necessary openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitable fixed all complete as per drawing and specification and direction. Rate to be inclusive of shadow profile at the junction of wall & ceiling, in between of ceiling, etc. complete. | SFT | 144.29 | 110 | 15871.9
Misc.
19 | Framed Artwork | Supplying & fixing approved framed artwork by the architect or the designer under the supervision of the site engineer. | Nos |  | 0 | 0
20 | Waterproofing | Providing and laying a proprietary chemical waterproofing system consisting of polymer-modified acrylic base coating in two coats in the form of a slurry (total consumption of 1.5 Kg/Sqm) as approved by the PM and as directed by the approved manufacturer of waterproofing coating, with sandwiched fiber mesh and protective screed. The work shall include cleaning the surface, grouting porous surfaces making ‘V’ grooves at junctions, cracks with nonshrink crystalline base cementitious grout, etc. Further including horizontal and vertical surfaces protected with 20mm screeding in 1:4 mortar (1 cement: 4 sand), finished in ready to receive Architectural finish, in the correct line, level, and plumb, curing, grouting, testing, etc. all complete to the entire satisfaction of the PM. | SFT | 184.79 | 80 | 14783.2
21 | Acrylic signage | Acrylic signage font backlit with led modules and fixed on the bulkhead as per the design and specifications. | LS |  | 0 | 0
|  | TOTAL AMOUNT |  | ANNEXURE AMOUNT-1 |  | 99774.9

## Giani C&I JMS
SR.NO. | ITEM | DESCRIPTION | UNIT | QTY. | NO | LENGTH | WIDTH/H | EXECUTED QTY | RATE | AMOUNT | REMARK
1 | Kitchen equipments unloading/ shifting | Unloading/Shifitng/ fixing of kitchen equipments. | JOB | 1 |  |  |  |  | 0 | 0
Civil works
2 | Internal Plaster | P&A of single coat backing plaster of 15-18 mm thick in CM 1:4 proportion to the walls & others surface including scaffolding, curing the joints, etc. The rates are inclusive of providing chicken mesh of 18mm gauge & 150mm width at junction of brick & RCC etc. at the walls, columns, beams etc., seven days water treatment as anti crack of plaster. Complete as per site engineer's instruction. | Sq.Ft | 682 |  |  |  | 0 |  | 0
Store entry lhs and rhs wall
store entry wall
Less door
3 | Half brick partition walls | Providing and laying 4 1/2" thick half brickwork in partition walls and architectural elements etc., with well burnt 1st class table moulded, good quality approved bricks in 1:4 Cement Mortar (1 Cement : 4 Coarse Sand by volume) including soaking the bricks in water adequately and drying, scaffolding, curing, rubbing the surface, raking out the joints etc., complete as directed and specified. | Sq.Ft | 35 |  |  |  | 4.575 |  | 0
|  | Counter back wall flap door opening closed |  |  | 1 | 1.83 | 2.5 | 4.575 |  |  |  | OK
4 | PCC Work | Providing and laying up to 50-75 mm thick cement concrete flooring with 1:2:4 cement concrete laid to proper level and slope in alternate bays including compactions, filling joints, or as directed, finishing smooth with cement Mortar 1:1 of sufficient minimum thickness to give a smooth & even surface and curing etc. complete as per architects instructions. | Sq.Ft | 173 |  |  |  | 140.04 | 0 | 0
|  | All store area |  |  | 1 | 18 | 7.78 | 140.04 |  |  |  | OK
5 | COBA Work | CINDER BLOCK COBA of Avg. thickness mentioned below; After laying of soil pipes, floor traps is completed the floor of the sunken portion shall be covered with cinder coba embedded manually with 15-20 mm wide joints in 20 mm thk. Waterproofing mortar 1:4 ( 1 cement : 4 coarse sand )in layers upto the full ht. of sunken portion, having top layer of 50 mm thk waterproof mortar 1:4 ( 1 cement : 4 coarse sand ) using specialized W.P. chemical, finished smooth / rough with floating coat of neat cement all complete and as per specification. | Sq.Ft | 173 |  |  |  | 140.04 | 0 | 0 |  | ok
|  | All store area |  |  | 1 | 18 | 7.78 | 140.04
6 | Kota Skirting | Fixing & laying of 150mm high kota stone for skirting with bedding of appropriate approved make adhesive & colour joint filler inclusive of making all groove/chamfering/rounding/hole where ever required, in proper line and level in all direction, polishing/finishing/cleaning etc. Complete as per detail drawing, specification and as directed by PMC. | RFT | 53 |  |  |  | 41 | 0 | 0
|  | Store entry lhs and rhs wall |  |  | 2 | 18 |  | 36 |  |  |  | OK
|  | store entry wall |  |  | 1 | 8 |  | 8 |  |  |  | OK
|  | Less door |  |  | -1 | 3 |  | -3 |  |  |  | OK
8 | SS Corner Guard | P&F of 304 grade 3mm thick SS Corner guard (30mm x 30mm), finished as per approved sample fixing with SS full thread screws on each corner of the kitchen's wall before cladding of tiles, so that the corner may be protected from damage. Complete in proper line &level and site engineer's instruction. | RFT | 43 |  |  |  |  | 0 | 0
Flooring & Cladding
11 | Kota Flooring | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : | SFT | 173 |  |  |  | 144.29 | 0 | 0
|  | All floor area |  |  | 1 | 18 | 7.78 | 140.04 |  |  |  | OK
|  | Below entry door |  |  | 1 | 1 | 4.25 | 4.25 |  |  |  | OK
14 | Subway Wall Tile Cladding -2 | Providing and fixing in subway tile of approved make & shade on any surface as per details in drawing and Over 12 mm thk bed of cement mortar 1:3 (cement: fine sand ) with thick grey cement slurry, with hairline joints using cement grout. The job includes cutting tiles & making smooth edges wherever required. The work shall also include the cost of materials, wastages, labor, all lead and lift at all levels, loading and unloading, transportation, curing, etc., and all other incidental charges, etc. Complete as specified in the drawing & to the satisfaction of the Site Engineer. Ceramic wall tile (Printed) With customized line work Make: -Johnson in exposed area / Ceramic wall tile white/ Satin white 75x300mm below the counter or hidden area | SFT | 210 |  |  |  | 136.9 | 0 | 0
|  | Store entry rhs and lhs |  |  | 1 | 3.7 | 18 | 66.6
[5 empty] | 1 | 3.7 | 19 | 70.3
16 | Wall Textured Paint | Providing & applying two or more coats of Textured paint/surface coating of approved make and shade over walls etc. after preparing the surface with a coat of primer and 4-6mm thick plaster of Paris punning to give a smooth and even surface etc. | SFT | 317 |  |  |  |  | 0 | 0
17 | Wooden beading work | Providing and fixing solid teak wood fixed on wall. Size: 50 x 18mm as per detail drawing. Finished with clear Melamine Polish in matte finish. | RFT | 51
Ceiling
18 | Gypsum false ceiling (MOH area) | Gypsum Board false Ceiling: Providing, fabrication and fixing in position of false ceiling ( height will be decided on the spot as per site conditions) by fixing 12 mm Th. Gypsum Board sheets on frame work of GI sheet section. The main runners of 22 gauge GI sheet and cross runners of 24 gauge GI sheet must be framed to form a mesh of 2’0”x2’0” c/c. The Gypsum Board must be fixed to the GI frame and joint to be properly filled in with POP paste and paper tape to get a leveled smooth ceiling. Recessing of the Gypsum Board for light fixtures must be done along with extra frame work of GI sheet section to hold the concealed light fixtures etc. directed by the site engineer. Including two coats of primer suitable for gypsum board two or more coats of plastic emulsion paint of approved shade and also including making necessary openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitable fixed all complete as per drawing and specification and direction. Rate to be inclusive of shadow profile at the junction of wall & ceiling, in between of ceiling, etc. complete. | SFT | 173 |  |  |  | 144.29 | 0 | 0
|  | All store area |  |  | 1 | 18 | 7.78 | 140.04 |  |  |  | OK
|  | Below entry door |  |  | 1 | 1 | 4.25 | 4.25 |  |  |  | OK
Misc.
19 | Framed Artwork | Supplying & fixing approved framed artwork by the architect or the designer under the supervision of the site engineer. | Nos | 2 |  |  |  |  | 0 | 0
20 | Waterproofing | Providing and laying a proprietary chemical waterproofing system consisting of polymer-modified acrylic base coating in two coats in the form of a slurry (total consumption of 1.5 Kg/Sqm) as approved by the PM and as directed by the approved manufacturer of waterproofing coating, with sandwiched fiber mesh and protective screed. The work shall include cleaning the surface, grouting porous surfaces making ‘V’ grooves at junctions, cracks with nonshrink crystalline base cementitious grout, etc. Further including horizontal and vertical surfaces protected with 20mm screeding in 1:4 mortar (1 cement: 4 sand), finished in ready to receive Architectural finish, in the correct line, level, and plumb, curing, grouting, testing, etc. all complete to the entire satisfaction of the PM. | SFT | 173 |  |  |  | 184.79 | 0 | 0
|  | All store area |  |  | 1 | 18 | 7.78 | 140.04 |  |  |  | OK
|  | Below entry door |  |  | 1 | 1 | 4.25 | 4.25 |  |  |  | OK
|  | On wall |  |  | 1 | 1 | 18 | 18 |  |  |  | OK
|  | NEXT WALL |  |  | 1 | 1 | 19 | 19 |  |  |  | OK
|  | NEXT WALL |  |  | 1 | 1 | 3.5 | 3.5 |  |  |  | OK
NEXT WALL
21 | Acrylic signage | Acrylic signage font backlit with led modules and fixed on the bulkhead as per the design and specifications. | LS | 1 |  |  |  |  | 0 | 0
TOTAL
GST EXTRA @ 18%
|  | GR. TOTAL | [7 empty] | 0

## GIANI PLUMBING BOQ
UNA FOOD COURT
DRAINAGE & WATER SUPPLY WORK BOQ
OUTLET-2 GIAN'S
S. No. | Description | Unit | EXECUTED QTY | ANNEXURE RATE | ANNEXURE AMOUNT
A | WATER SUPPLY PIPING
1 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes SDR 11, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. (Concealed work including cutting chases and making good the walls etc.,) Pressure Testing (Pipe shall be tested with 1.5 times working pressure as covered in specifications)
1.1 | 15 mm Dia | R.mt | 19 | 330 | 6270
1.2 | 20 mm Dia | R.mt | 2.37 | 420 | 995.4
1.3 | 25 mm Dia | R.mt
1.4 | 32mm Dia | R.mt
2 | Providing & fixing gun metal lever operated ball valve. Tested to a pressure of 15 Kg / Sqcm. Including flanges/union, nuts, bolts, washer etc. Complete as required.
2.1 | 20mm Dia | Nos. | 1 | 1250 | 1250
2.2 | 25mm Dia | Nos.
2.3 | 32mm Dia | Nos.
2.4 | 40mm Dia | Nos.
3 | Providing, fixing, testing and commissioning of NRV with forged brass body, brass diaphram and SS seal in water supply pipes. Complete as required.
3.1 | 25mm Dia | Nos.
4 | Providing, fixing, testing and commissioning of Y STRAINER FLANGED END EPOXY COATED WITH SS SCREEN (CR16B)
4.1 | 25mm Dia | Nos.
5 | Providing and fixing of brass multijet water meters with magnetic transmision of IS-779:1994 including with rubber gasket, flanges/ unions, nuts, bolts, washers, etc. complete as required. Make : Kranti
5.1 | 25 mm Dia incoming line | Nos.
5.2 | 32 mm Dia incoming line | Nos.
5.3 | 40 mm Dia incoming line | Nos.
6 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories
6.1 | 3 L Capacity- | Nos.
6.2 | 20 L Capacity | Nos.
6.3 | 25 L Capacity- | Nos.
7 | SITC of Eco smart RO 50 LPH Capacity with all required accessories | Nos
8 | SITC of grease trap -model NGT-14 Capacity -25.5 lit ( 28 LPM) with all required accessories( SIZE:- | Nos
9 | SITC of grease trap -model NGT-30 Capacity -47.5 lit ( 57 LPM) with all required accessories( SIZE:- | Nos
B | DRAINAGE
1 | Providing and fixing Upvc SWR pipes ( Class B Heavy Type) including all fittings (plain or door) e.g. bends, junction, cowls, offsets, access pieces, jointing with rubber ring/solvent cement joints,jali,clamps including cutting chase or holes in walls and floors and making good where required.( Inside the building)
1.1 | 50mm Dia | R.mt
1.2 | 75mm Dia | R.mt | 7.7 | 405 | 3542
1.3 | 110 mm Dia | R.mt
1.4 | 150 mm Dia | R.mt
2 | Providing & fixing in position pipe trap of self cleaning design of following sizes for the embedded areas. Making proper connection with , cutting chase / hole in floors /slabs and bringing the same in proper condition in cement concrete 1:2:4 mix complete as required. including cost of cutting and making good the walls and floors where required. Make :
2.1 | P-trap 110 mm dia | Each
2.2 | Multi trap 110 mm dia with square grating (Outlet 75MM dia) | Each
2.3 | Floor trap 110 mm dia with grating(Outlet 75MM dia) | Each | 3 | 1250 | 3750
2.4 | Nahani trap 110 mm dia with grating(Outlet 75MM dia) | Each
C | SANITARY AND C. P. FITTINGS & FIXTURES
Only installation, testing and commissioning of sanitary and C.P. fittings
1.1 | Providing and Fixing of S.S. sink without drain board over all size 450Wx700Dx900H mm Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos
1.2 | Providing and Fixing of RO S.S. sink without drain board over all size 600Wx700Dx850H mm +200 High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos
1.3 | Providing and Fixing of S.S. sink without drain board over all size 450Wx450Dx850H mm High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos
1.4 | Providing and Fixing of Three Bowl S.S. sink without drain board over all size 1500Wx700Dx850H mm +100 High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos
|  |  | 1 | 5500 | 5500
1.2 | Providing and Fixing C.P. brass wall mounted/ table top sink mixer with swinging spout, wall mounted type complete as required. | Nos | 3 | 1250 | 3750
1.4 | Angle Cock with PVC pipe connection upto sink/Geyser /RO connection | Nos
D | S.S. GRATING
SITC of , testing and commissioning of S.S.Gratings
|  |  | 1 | 5500 | 5500
1 | Making chamber in brick work including internal tiling etc for S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos.
GRAND - TOTAL A , B, C AND D
|  |  | ANNEXURE AMOUNT-1 |  | 30557.4

## GIANI PLUMBING JMS
S. No. | Description | Unit | Qty. | NO | LENGTH | EXECUTED QTY | REMARKS
A | WATER SUPPLY PIPING
1 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes SDR 11, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. (Concealed work including cutting chases and making good the walls etc.,) Pressure Testing (Pipe shall be tested with 1.5 times working pressure as covered in specifications)
1.1 | 15 mm Dia | R.mt | 0
1.2 | 20 mm Dia | R.mt | 17 |  |  | 19 |  | OK
| GianiS to BikanerVala main line |  |  | 1 | 6 | 6 |  | OK
| Vertival |  |  | 1 | 2 | 2 |  | OK
| Vertival |  |  | 4 | 2 | 8 |  | OK
| Next Wall |  |  | 2 | 1.5 | 3 |  | OK
1.3 | 25 mm Dia | R.mt | 7 |  |  | 2.37
| Handwash makeline |  |  | 1 | 2.37 | 2.37 |  | OK
1.4 | 32mm Dia | R.mt | 0
2 | Providing & fixing gun metal lever operated ball valve. Tested to a pressure of 15 Kg / Sqcm. Including flanges/union, nuts, bolts, washer etc. Complete as required.
2.1 | 20mm Dia | Nos. | 0
2.2 | 25mm Dia | Nos. | 2 |  |  | 1 |  | ok
2.3 | 32mm Dia | Nos. | 0
2.4 | 40mm Dia | Nos. | 0
3 | Providing, fixing, testing and commissioning of NRV with forged brass body, brass diaphram and SS seal in water supply pipes. Complete as required.
3.1 | 25mm Dia | Nos. | 1
4 | Providing, fixing, testing and commissioning of Y STRAINER FLANGED END EPOXY COATED WITH SS SCREEN (CR16B)
4.1 | 25mm Dia | Nos. | 1
5 | Providing and fixing of brass multijet water meters with magnetic transmision of IS-779:1994 including with rubber gasket, flanges/ unions, nuts, bolts, washers, etc. complete as required. Make : Kranti
5.1 | 25 mm Dia incoming line | Nos. | 1
5.2 | 32 mm Dia incoming line | Nos. | 0
5.3 | 40 mm Dia incoming line | Nos. | 0
6 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories
6.1 | 3 L Capacity- | Nos. | 1
6.2 | 20 L Capacity | Nos. | 0
6.3 | 25 L Capacity- | Nos. | 0
7 | SITC of Eco smart RO 50 LPH Capacity with all required accessories | Nos | 0
8 | SITC of grease trap -model NGT-14 Capacity -25.5 lit ( 28 LPM) with all required accessories( SIZE:- | Nos | 1
9 | SITC of grease trap -model NGT-30 Capacity -47.5 lit ( 57 LPM) with all required accessories( SIZE:- | Nos | 0
B | DRAINAGE
1 | Providing and fixing Upvc SWR pipes ( Class B Heavy Type) including all fittings (plain or door) e.g. bends, junction, cowls, offsets, access pieces, jointing with rubber ring/solvent cement joints,jali,clamps including cutting chase or holes in walls and floors and making good where required.( Inside the building)
1.1 | 50mm Dia | R.mt | 3
1.2 | 75mm Dia | R.mt | 1
1.3 | 110 mm Dia | R.mt | 5 |  |  | 7.7
| RHS TO LHS |  |  | 1 | 7.7 | 7.7 |  | Area details Required | already approved in JMS
1.4 | 150 mm Dia | R.mt | 0
2 | Providing & fixing in position pipe trap of self cleaning design of following sizes for the embedded areas. Making proper connection with , cutting chase / hole in floors /slabs and bringing the same in proper condition in cement concrete 1:2:4 mix complete as required. including cost of cutting and making good the walls and floors where required. Make :
2.1 | P-trap 110 mm dia | Each | 0
2.2 | Multi trap 110 mm dia with square grating (Outlet 75MM dia) | Each | 0
2.3 | Floor trap 110 mm dia with grating(Outlet 75MM dia) | Each | 0
2.4 | Nahani trap 110 mm dia with grating(Outlet 75MM dia) | Each | 1 |  |  | 3 |  | OK
C | SANITARY AND C. P. FITTINGS & FIXTURES
Only installation, testing and commissioning of sanitary and C.P. fittings
1.1 | Providing and Fixing of S.S. sink without drain board over all size 450Wx700Dx900H mm Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos | 1
1.2 | Providing and Fixing of RO S.S. sink without drain board over all size 600Wx700Dx850H mm +200 High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos | 0
1.3 | Providing and Fixing of S.S. sink without drain board over all size 450Wx450Dx850H mm High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos | 1
1.4 | Providing and Fixing of Three Bowl S.S. sink without drain board over all size 1500Wx700Dx850H mm +100 High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos | 0
1.2 | Providing and Fixing C.P. brass wall mounted/ table top sink mixer with swinging spout, wall mounted type complete as required. | Nos | 2 |  |  | 1 |  | OK
1.4 | Angle Cock with PVC pipe connection upto sink/Geyser /RO connection | Nos | 6 |  |  | 3 |  | OK
D | S.S. GRATING
SITC of , testing and commissioning of S.S.Gratings
1 | Making chamber in brick work including internal tiling etc for S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 2 |  |  | 1 | Without Grating | OK
GRAND - TOTAL A , B, C AND D

## GIANI ELECTRICAL BOQ
OUTLET GAINIS UNA FOOD COURT
BILL OF QUANTITIES FOR PANELS & DISTRIBUTION BOARDS - R0
DATE: 20.JAN.2024
SR. NO. | DESCRIPTION | UNIT | EXECUTED QTY | ANNEXURE RATE | ANNEXURE AMOUNT
1 | PANELS, SWITCHGEARS & DISTRIBUTION BOARD |  |  |  | 0
1.1 | MAIN PANEL-1 | Nos.
Incomer : 63 AMPS 4P MCCB, 25kA with TM Based O/C & SC Release.
Meter & Protection: ELR with CBCT; 60/5A, 15VA, CL-1 CT's -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
Indication: Phase indicating lamps with 6A MCB
Busbar: 100A TPN Cu Busbar
Outgoings:
a) 63A 4P MCCB, 16kA, TM BASED-1 Nos.
d) 40A DP MCB-2 Nos.
f) 32A 4P MCCB 16kA TM Based Releases with 1.5 kW DOL Starter, Phase Indicating lamps, ON/OFF/TRIP Indication, ON/OFF Push Button-1 Nos.
1.2 | MAIN PANEL-2 | Nos. |  |  | 0
Incomer : 40 AMPS 4P MCCB, 25kA with TM Based O/C & SC Release.
Meter & Protection: ELR with CBCT; 40/5A, 15VA, CL-1 CT's -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
Indication: Phase indicating lamps with 6A MCB
Busbar: 75A TPN Cu Busbar
Outgoings:
a) 32A 4P MCB, 10kA-1 Nos.
b) 25A 4P MCB, 10kA-1 Nos.
c) 32A DP MCB, 10kA-1 Nos.
d) 40A DP MCB, 10kA-1 Nos.
2 | SWITCHGEARS & DISTRIBUTION BOARD
Supplying & installing at site in positioning, connecting, testing and commissioning of the following type Distribution Boards & Switchgears. (IP-43) ACRY DB
Provide insulated dedicated earth link for UPS DB
All MCB's for UPS shall be D Curve, C Curve for Power & B Curve for Lighting.
2.1 | SWITCHGEARS
2.1.1 | Supply, installation, testing and commissioning of sheet metal enclosures for the following switchgears.
2.1.1.a | 63/40/32/20 amps 4P MCB 'C' TYPE with complete with all mounting accessories – for Indoor Legrand make | Nos.
2.1.1.b | 63/40/32/20 amps DP MCB 'C' TYPE with complete with all mounting accessories – IP-65
2.1.1.c | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos.
2.1.1.d | 25 amps DP MCB with 25A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. |  |  | 0
2.1.1.d | 16 amps DP MCB with 15A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. |  |  | 0
2.1.1.e | 5/15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos.
2.2 | DISTRIBUTION BOARDS
2.2.1 | 6 WAY SPN DB - UPS DB | Nos. |  |  | 0
Incomer : 20 AMPS DP MCB 10KA : 1 Nos.
Outgoings : 6/10/16 A SP MCB "B" Type - 4 Nos.
2.2.2 | 8 WAY TPN - LPDB | Nos. | 1 | 39000 | 39000
Incomer : 63A, FP, MCB, 10kA: 1 Nos
Sub Incomer : 40A, DP, RCCB, 100mA: 3 Nos
Outgoings : 10/16/20/25 A SP MCB "C" Type - 24 Nos.
Outgoings : 32 A SP MCB "C" Type - 0 Nos.
2.2.3 | 12 WAY SPN DB - UPS DB | Nos. | 0 |  | 0
Incomer : 32 AMPS DP RCBO 100mA
Outgoings : 10/16/20 A SP MCB "C" Type - 6 Nos.
TOTAL FOR DISTRIBUTION BOARDS
2 | MV CABLES
2.1 | POWER CABLING
Supply and laying, effecting proper connections, testing & commissioning of the following sizes of 1.1 KV XLPE FRLS armoured/ unarmoured PVC insulated PVC sheathed aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications.
2.1.1 | Aluminium cables
a | 4C x 50 Sq.mm. | Mtr. |  |  | 0
b | 3.5C x 35 Sq.mm. | Mtr. |  |  | 0
c | 4C x 10 Sq.mm. | Mtr. |  |  | 0
2.1.2 | - do - but for copper cables |  |  |  | 0
a | 4C x 25 Sq.mm. | Mtr. |  |  | 0
b | 4C x 16 Sq.mm. | Mtr. | 65 | 350 | 22750
c | 4C x 10 Sq.mm. | Mtr. |  |  | 0
d | 4C x 6 Sq.mm. | Mtr. |  |  | 0
e | 4C x 4 Sq.mm. | Mtr. |  |  | 0
f | 4C x 2.5 Sq.mm. | Mtr. |  |  | 0
g | 3C x 6 Sq.mm. | Mtr. |  |  | 0
h | 3C x 4 Sq.mm. | Mtr. |  |  | 0
i | 3C x 2.5 Sq.mm. | Mtr. |  |  | 0
2.1.3 | CU Flexible Cables |  |  |  | 0
a | 4C x 6 Sq.mm. | Mtr. |  |  | 0
b | 4C x 4 Sq.mm. | Mtr. |  |  | 0
c | 3C x 4 Sq.mm. | Mtr. |  |  | 0
d | 3C x 2.5 Sq.mm. | Mtr. |  |  | 0
e | 2C x 2.5 Sq.mm. for Earthing | Mtr. |  |  | 0
2.1.4 | , - do - but for copper flexible cables
a | 1c x 4 Sq.mm PVC insulated PVC flexible copper conductor cables alongwith termination (GREEN COLOUR) | Mtr.
TOTAL FOR POWER CABLES
2.2 | CABLE TERMINATION
Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper.
a | 4C x 50 Sq.mm. AL | Nos. |  |  | 0
b | 3.5C x 35 Sq.mm. | Nos. |  |  | 0
c | 4C x 10 Sq.mm. | Nos. |  |  | 0
d | 4C x 16 Sq.mm. CU | Nos. | 2 | 400 | 800
e | 4C x 10 Sq.mm. | Nos. |  |  | 0
f | 4C x 6 Sq.mm. | Nos. |  |  | 0
g | 4C x 4 Sq.mm. | Nos. |  |  | 0
h | 4C x 2.5 Sq.mm. | Nos. |  |  | 0
i | 3C x 6 Sq.mm. | Nos. |  |  | 0
j | 3C x 4 Sq.mm. | Nos. |  |  | 0
k | 3C x 2.5 Sq.mm. | Nos. |  |  | 0
l | Flexible cable |  |  |  | 0
m | 4C x 6 Sq.mm. | Nos. |  |  | 0
n | 4C x 4 Sq.mm. | Nos. |  |  | 0
o | 3C x 4 Sq.mm. | Nos. |  |  | 0
p | 3C x 2.5 Sq.mm. (Lighting) | Nos. |  |  | 0
q | 2C x 2.5 Sq.mm. | Nos. |  |  | 0
TOTAL FOR POWER CABLE TERMINATION
TOTAL FOR CABLES & TERMINATION
3 | RACEWAYS AND CABLE TRAYS
3.1 | TRUNKING: Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick G.I. Trunking of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick G.I. coupler plates & Reducers as per requirement. The cost shall including all supporting and fixing accessories with 8/10mm threaded Ros & Clamps etc. including dash fasteners.
a | 100 mm (wide) x 100 mm (height) | Mtr.
b | 50 mm (wide) x 50 mm (height) | Mtr.
3.2 | RACEWAY: Fabricating, supplying to site of installation, installation in the floor before the flooring from 2 mm thick pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick. The raceways shall be clamped to the floor slab with GI clamps 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI cover which will be nut bolted to the Junction box to cover the entire Junction box side walls complete as required etc. all the Raceways sections shall be earthed.
a | 100 mm (wide) x 40 mm (height) | Mtr.
b | 65 mm (wide) x 40 mm (height) | Mtr.
3.3 | JUNCTION BOXES: Fabricating supplying to site of installation, Junction boxes made from 2 mm thick pregalvanised sheet, with 3.0 mm thick pregalvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The floor junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc.
(variation in height may be considered for quoting as floor thickness may vary)
a | 250 mm x 250 x 60/50 mm (height) | Mtr.
b | 150 mm x 150 x 60/50 mm (height) | Mtr.
c | 100 mm x 150 x 60/50 mm (height) | Mtr.
3.4 | CABLE TRAY: Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same)
a | 300 mm wide x 50 mm x 2.0 mm thk | Mtr.
b | 150 mm wide x 50 mm x 2.0 mm thk | Mtr.
c | 100 mm wide x 50 mm x 2.0 mm thk | Mtr.
d | 50 mm wide x 50 mm x 2.0 mm thk | Mtr.
| TOTAL FOR RACEWAYS AND CABLE TRAYS |  |  | Rs.
4 | POINT WIRING
Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr.
The secondary/Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr.
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
The Length shall be paid as per the actual measurements & as per following manner.
4.1 | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling/walls/ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates shall exclusive of Switches & Switch boxes.
4.1.1 | From DB to Normal Switch Board | Nos. | 2 |  | 0
4.1.2 | From DB to Emergency Switch Board | Nos. | 2 |  | 0
4.2 | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling/walls/ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required from the above switch board. Rates shall exclusive of Switches & Switch Box. (FROM SB TO LIGHT)
4.2.1 | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 3 |  | 0
4.2.2 | First point controlled by one no. 6 amp switch. (upto 20Mtr.) | Nos.
4.2.3 | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. |  |  | 0
4.2.4 | First point controlled by one no. 6 amp switch. For Emergency Light (upto 20Mtr.) | Nos.
4.3 | Same as item No. 4.2.1 & 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed GI conduit and earthing | Nos. | 6 |  | 0
4.4 | Same as item No. 4.2.3 & 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed GI conduit and earthing For Emergency Light | Nos. |  |  | 0
4.5 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed GI conduits as called for and earthing.
4.5.1 | First point controlled by existing MCB in D.B. | Nos.
4.5.2 | First Emergency point controlled by existing MCB in D.B. | Nos.
4.6 | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed/exposed GI conduit and earthing | Nos.
4.7 | Same as item No. 4.5.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing For Emergency Lighting | Nos.
4.8 | Wiring for UPS/Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. |  |  | 0
4.9 | Wiring for UPS/Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | Mtr.
4.1 | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling/wall/floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the length of conduit.
4.10.1 | 20 mm dia GI Conduit | Mtr. |  |  | 0
4.10.2 | 25 mm dia GI Conduit | Mtr. |  |  | 0
4.11 | Providing and fixing in position the following GI FLEXIBLE conduits including all accessories concealed in F. ceiling/wall/floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the length of conduit.
4.11.1 | 20 mm dia GI Conduit | Mtr.
4.11.2 | 25 mm dia GI Conduit | Mtr. |  |  | 0
4.12 | Supply & Laying of 2Cx2.5 Sq.mm FRLS Cu Flexible Cable in 25mm dia. GI Conduit for CCTV | Mtr.
TOTAL FOR POINT WIRING
5 | MODULAR SWITCHES
5.1 | Supply, installation, testing & commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches & earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.(Make- Legrand Aretor Series)
5.1.1 | 6A One Way Switch | Nos. | 3 | 350 | 1050
5.1.2 | 6A 5 pin Socket - 1Nos. & 6A Switch - 1Nos. | Nos. | 4 | 400 | 1600
5.1.3 | 6/16A Socket outlet - 1Nos. & 16A Switch - 1Nos.(Raw/UPS Power) | Nos. | 8 | 500 | 4000
5.1.4 | 5/15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos.
5.1.5 | 20 Amp 1- Ph Industrial Socket (Metal Clad) | Nos. |  |  | 0
5.1.5 | 32 Amp 3- Ph Industrial Socket (Metal Clad) | Nos. |  |  | 0
5.1.6 | 20 Amp 1- Ph Electrical Outlet | Nos. |  |  | 0
5.1.7 | Data Outlet (RJ-45) | Nos. |  |  | 0
5.1.8 | Telephone Outlet (RJ-11) | Nos. |  |  | 0
TOTAL FOR MODULAR SWITCHES
7 | LIGHT FIXTURES INSTALLATION
7.1 | Receiving from Store, Installation, testing & commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook/Rods as per final approval from Architect/Client/Consultant
7.1.1 | ROUND CEILING LIGHT-18 WATT | Nos. | 9 | 350 | 3150
7.1.2 | PENDENT LIGHT | Nos.
7.1.3 | HANGING LIGHT | Nos.
7.1.4 | TRACK LIGHT | Nos.
7.1.6 | LED STRIP (15 M) | Mtr.
7.1.7 | WALL LIGHT | Nos.
TOTAL FOR LIGHT FIXTURE
8 | MISCELLANEOUS WORKS
8.1 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. |  |  | 0
8.2 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. |  |  | 0
8.3 | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical & ELV Services executed at site. | Part of Tender
72350
TOTAL AMOUNT |  |  | ANNEXURE AMOUNT-1 |  | 72350

## GIANI ELECTRICAL JMS
SR. NO. | DESCRIPTION | UNIT | BOQ QTY | NO | LENGTH | EXECUTED QTY | RATE IN Rs. | TOTAL AMOUNT
1 | PANELS, SWITCHGEARS & DISTRIBUTION BOARD
1.1 | MAIN PANEL-1 | Nos. | 0 |  |  |  |  | 0
Incomer : 63 AMPS 4P MCCB, 25kA with TM Based O/C & SC Release.
Meter & Protection: ELR with CBCT; 60/5A, 15VA, CL-1 CT's -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
Indication: Phase indicating lamps with 6A MCB
Busbar: 100A TPN Cu Busbar
Outgoings:
a) 63A 4P MCCB, 16kA, TM BASED-1 Nos.
d) 40A DP MCB-2 Nos.
f) 32A 4P MCCB 16kA TM Based Releases with 1.5 kW DOL Starter, Phase Indicating lamps, ON/OFF/TRIP Indication, ON/OFF Push Button-1 Nos.
1.2 | MAIN PANEL-2 | Nos. | 0 |  |  |  |  | 0
Incomer : 40 AMPS 4P MCCB, 25kA with TM Based O/C & SC Release.
Meter & Protection: ELR with CBCT; 40/5A, 15VA, CL-1 CT's -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
Indication: Phase indicating lamps with 6A MCB
Busbar: 75A TPN Cu Busbar
Outgoings:
a) 32A 4P MCB, 10kA-1 Nos.
b) 25A 4P MCB, 10kA-1 Nos.
c) 32A DP MCB, 10kA-1 Nos.
d) 40A DP MCB, 10kA-1 Nos.
2 | SWITCHGEARS & DISTRIBUTION BOARD
Supplying & installing at site in positioning, connecting, testing and commissioning of the following type Distribution Boards & Switchgears. (IP-43) ACRY DB
Provide insulated dedicated earth link for UPS DB
All MCB's for UPS shall be D Curve, C Curve for Power & B Curve for Lighting.
2.1 | SWITCHGEARS
2.1.1 | Supply, installation, testing and commissioning of sheet metal enclosures for the following switchgears.
2.1.1.a | 63/40/32/20 amps 4P MCB 'C' TYPE with complete with all mounting accessories – for Indoor Legrand make | Nos. | [5 empty] | 0
2.1.1.b | 63/40/32/20 amps DP MCB 'C' TYPE with complete with all mounting accessories – IP-65 |  | 0 |  |  |  |  | 0
2.1.1.c | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0 |  |  |  |  | 0
2.1.1.d | 25 amps DP MCB with 25A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | [5 empty] | 0
2.1.1.d | 16 amps DP MCB with 15A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0 |  |  |  |  | 0
2.1.1.e | 5/15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0 |  |  |  |  | 0
2.2 | DISTRIBUTION BOARDS
2.2.1 | 6 WAY TPN DB - UPS DB- 6 WAY VTPN DB - USED NOT 8 WAY | Nos. | 0 |  |  | 1 |  | 0 | There is VTPN DB
| Incomer : 40 AMPS FP MCB 10KA : 1 Nos. | [7 empty] | 6 WAY VTPN DB - USED NOT 8 WAY OR NOT IN BOQ ADD IN EXTRA ITEMS
Outgoings : 6/10/16 A SP MCB "B" Type - 11 Nos.
2.2.2 | 8 WAY TPN - LPDB | Nos. | 1 |  |  |  |  | 0
Incomer : 63A, FP, MCB, 10kA: 1 Nos
Sub Incomer : 40A, DP, RCCB, 100mA: 3 Nos
Outgoings : 10/16/20/25 A SP MCB "C" Type - 24 Nos.
Outgoings : 32 A SP MCB "C" Type - 0 Nos.
2.2.3 | 12 WAY SPN DB - UPS DB | Nos. | 0 |  |  |  |  | 0
Incomer : 32 AMPS DP RCBO 100mA
Outgoings : 10/16/20 A SP MCB "C" Type - 6 Nos.
| TOTAL FOR DISTRIBUTION BOARDS | [5 empty] | Rs. | 0
2 | MV CABLES
2.1 | POWER CABLING
Supply and laying, effecting proper connections, testing & commissioning of the following sizes of 1.1 KV XLPE FRLS armoured/ unarmoured PVC insulated PVC sheathed aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications.
2.1.1 | Aluminium cables
a | 4C x 50 Sq.mm. | Mtr. | [5 empty] | 0
b | 3.5C x 35 Sq.mm. | Mtr. | [5 empty] | 0
c | 4C x 10 Sq.mm. | Mtr. | [5 empty] | 0
2.1.2 | - do - but for copper cables
a | 4C x 25 Sq.mm. | Mtr. | [5 empty] | 0
b | 4C x 16 Sq.mm. | Mtr. |  |  |  | 65 |  | 0 | OK
DB to tearrace panel (2+2.5+3+4+3+8+18+6+5+5+3+3+2.5)
c | 4C x 10 Sq.mm. | Mtr. | 20 |  |  |  |  | 0
d | 4C x 6 Sq.mm. | Mtr. | [5 empty] | 0
e | 4C x 4 Sq.mm. | Mtr. | [5 empty] | 0
f | 4C x 2.5 Sq.mm. | Mtr. | [5 empty] | 0
g | 3C x 6 Sq.mm. | Mtr. | [5 empty] | 0
h | 3C x 4 Sq.mm. | Mtr. | [5 empty] | 0
i | 3C x 2.5 Sq.mm. | Mtr. | [5 empty] | 0
2.1.3 | CU Flexible Cables
a | 4C x 6 Sq.mm. | Mtr. | [5 empty] | 0
b | 4C x 4 Sq.mm. | Mtr. | [5 empty] | 0
c | 3C x 4 Sq.mm. | Mtr. | [5 empty] | 0
d | 3C x 2.5 Sq.mm. | Mtr. | [5 empty] | 0
e | 2C x 2.5 Sq.mm. for Earthing | Mtr. | [5 empty] | 0
2.1.4 | , - do - but for copper flexible cables
a | 1c x 4 Sq.mm PVC insulated PVC flexible copper conductor cables alongwith termination (GREEN COLOUR) | Mtr. | [5 empty] | 0
| TOTAL FOR POWER CABLES | [6 empty] | 0
2.2 | CABLE TERMINATION
Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper.
a | 4C x 50 Sq.mm. AL | Nos. | [5 empty] | 0
b | 3.5C x 35 Sq.mm. | Nos. | [5 empty] | 0
c | 4C x 10 Sq.mm. | Nos. | [5 empty] | 0
d | 4C x 16 Sq.mm. CU | Nos. |  |  |  | 2 |  | 0 | OK
e | 4C x 10 Sq.mm. | Nos. | 2 |  |  |  |  | 0
f | 4C x 6 Sq.mm. | Nos. | [5 empty] | 0
g | 4C x 4 Sq.mm. | Nos. | [5 empty] | 0
h | 4C x 2.5 Sq.mm. | Nos. | [5 empty] | 0
i | 3C x 6 Sq.mm. | Nos. | [5 empty] | 0
j | 3C x 4 Sq.mm. | Nos. | [5 empty] | 0
k | 3C x 2.5 Sq.mm. | Nos. | [5 empty] | 0
l | Flexible cable
m | 4C x 6 Sq.mm. | Nos. | [5 empty] | 0
n | 4C x 4 Sq.mm. | Nos. | [5 empty] | 0
o | 3C x 4 Sq.mm. | Nos. | [5 empty] | 0
p | 3C x 2.5 Sq.mm. (Lighting) | Nos. | [5 empty] | 0
q | 2C x 2.5 Sq.mm. | Nos. | [5 empty] | 0
| TOTAL FOR POWER CABLE TERMINATION | [6 empty] | 0
| TOTAL FOR CABLES & TERMINATION | [5 empty] | Rs. | 0
3 | RACEWAYS AND CABLE TRAYS
3.1 | TRUNKING: Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick G.I. Trunking of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick G.I. coupler plates & Reducers as per requirement. The cost shall including all supporting and fixing accessories with 8/10mm threaded Ros & Clamps etc. including dash fasteners.
a | 100 mm (wide) x 100 mm (height) | Mtr. | [5 empty] | 0
b | 50 mm (wide) x 50 mm (height) | Mtr. | [5 empty] | 0
3.2 | RACEWAY: Fabricating, supplying to site of installation, installation in the floor before the flooring from 2 mm thick pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick. The raceways shall be clamped to the floor slab with GI clamps 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI cover which will be nut bolted to the Junction box to cover the entire Junction box side walls complete as required etc. all the Raceways sections shall be earthed.
a | 100 mm (wide) x 40 mm (height) | Mtr. | 0 |  |  |  |  | 0
b | 65 mm (wide) x 40 mm (height) | Mtr. | [5 empty] | 0
3.3 | JUNCTION BOXES: Fabricating supplying to site of installation, Junction boxes made from 2 mm thick pregalvanised sheet, with 3.0 mm thick pregalvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The floor junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc.
(variation in height may be considered for quoting as floor thickness may vary)
a | 250 mm x 250 x 60/50 mm (height) | Mtr. | [5 empty] | 0
b | 150 mm x 150 x 60/50 mm (height) | Mtr. | [5 empty] | 0
c | 100 mm x 150 x 60/50 mm (height) | Mtr. | 0 |  |  |  |  | 0
3.4 | CABLE TRAY: Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same)
a | 300 mm wide x 50 mm x 2.0 mm thk | Mtr. | [5 empty] | 0
b | 150 mm wide x 50 mm x 2.0 mm thk | Mtr. | 10 |  |  |  |  | 0
c | 100 mm wide x 50 mm x 2.0 mm thk | Mtr. | [5 empty] | 0
d | 50 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0 |  |  |  |  | 0
| TOTAL FOR RACEWAYS AND CABLE TRAYS | [5 empty] | Rs. | 0
4 | POINT WIRING
Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr.
The secondary/Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr.
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
The Length shall be paid as per the actual measurements & as per following manner.
4.1 | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling/walls/ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates shall exclusive of Switches & Switch boxes.
4.1.1 | From DB to Normal Switch Board | Nos. | 5 |  |  | 2 |  | 0 | OK
4.1.2 | From DB to Emergency Switch Board | Nos. | 0 |  |  | 2 |  | 0 | OK
4.2 | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling/walls/ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required from the above switch board. Rates shall exclusive of Switches & Switch Box. (FROM SB TO LIGHT)
4.2.1 | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 3 |  |  | 3 |  | 0 | OK
4.2.2 | First point controlled by one no. 6 amp switch. (upto 20Mtr.) | Nos. | [5 empty] | 0
4.2.3 | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. | 2 |  |  |  |  | 0
4.2.4 | First point controlled by one no. 6 amp switch. For Emergency Light (upto 20Mtr.) | Nos. | [5 empty] | 0
4.3 | Same as item No. 4.2.1 & 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed GI conduit and earthing | Nos. | 3 |  |  | 6 |  | 0 | OK
4.4 | Same as item No. 4.2.3 & 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed GI conduit and earthing For Emergency Light | Nos. | 2 |  |  |  |  | 0
4.5 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed GI conduits as called for and earthing.
4.5.1 | First point controlled by existing MCB in D.B. | Nos. | 0 |  |  |  |  | 0
4.5.2 | First Emergency point controlled by existing MCB in D.B. | Nos. | 0 |  |  |  |  | 0
4.6 | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed/exposed GI conduit and earthing | Nos. | 0 |  |  |  |  | 0
4.7 | Same as item No. 4.5.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing For Emergency Lighting | Nos. | 0 |  |  |  |  | 0
4.8 | Wiring for UPS/Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. | 175 |  |  |  |  | 0
4.9 | Wiring for UPS/Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. | [5 empty] | 0
4.1 | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling/wall/floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the length of conduit.
4.10.1 | 20 mm dia GI Conduit | Mtr. | 80 |  |  |  |  | 0
4.10.2 | 25 mm dia GI Conduit | Mtr. | 50 |  |  |  |  | 0
4.11 | Providing and fixing in position the following GI FLEXIBLE conduits including all accessories concealed in F. ceiling/wall/floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the length of conduit.
4.11.1 | 20 mm dia GI Conduit | Mtr. | [5 empty] | 0
4.11.2 | 25 mm dia GI Conduit | Mtr. | 25 |  |  |  |  | 0
4.12 | Supply & Laying of 2Cx2.5 Sq.mm FRLS Cu Flexible Cable in 25mm dia. GI Conduit for CCTV | Mtr. | 0 |  |  |  |  | 0
| TOTAL FOR POINT WIRING | [5 empty] | Rs. | 0
5 | MODULAR SWITCHES
5.1 | Supply, installation, testing & commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches & earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.(Make- Legrand Aretor Series)
5.1.1 | 6A One Way Switch | Nos. | 12 |  |  | 3 |  | 0 | OK
5.1.2 | 6A 5 pin Socket - 1Nos. & 6A Switch - 1Nos. | Nos. | 7 |  |  | 4 |  | 0 | OK
5.1.3 | 6/16A Socket outlet - 1Nos. & 16A Switch - 1Nos.(Raw/UPS Power) | Nos. | 4 |  |  | 8 |  | 0 | OK
5.1.4 | 5/15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0 |  |  |  |  | 0
5.1.5 | 20 Amp 1- Ph Industrial Socket (Metal Clad) | Nos. | 3 |  |  |  |  | 0
5.1.5 | 32 Amp 3- Ph Industrial Socket (Metal Clad) | Nos. | 0 |  |  |  |  | 0
5.1.6 | 20 Amp 1- Ph Electrical Outlet | Nos. | 1 |  |  |  |  | 0
5.1.7 | Data Outlet (RJ-45) | Nos. | 2 |  |  |  |  | 0
5.1.8 | Telephone Outlet (RJ-11) | Nos. | 2 |  |  |  |  | 0
| TOTAL FOR MODULAR SWITCHES | [5 empty] | Rs. | 0
7 | LIGHT FIXTURES INSTALLATION
7.1 | Receiving from Store, Installation, testing & commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook/Rods as per final approval from Architect/Client/Consultant
7.1.1 | ROUND CEILING LIGHT-18 WATT | Nos. | 10 |  |  | 9 |  | 0 | OK
7.1.2 | PENDENT LIGHT | Nos. | [5 empty] | 0
7.1.3 | HANGING LIGHT | Nos. | [5 empty] | 0
7.1.4 | TRACK LIGHT | Nos. | [5 empty] | 0
7.1.6 | LED STRIP (15 M) | Mtr. | [5 empty] | 0
7.1.7 | WALL LIGHT | Nos. | [5 empty] | 0
| TOTAL FOR LIGHT FIXTURE | [5 empty] | Rs. | 0
8 | MISCELLANEOUS WORKS
8.1 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  |  |  |  | 0
8.2 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 |  |  |  |  | 0
8.3 | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical & ELV Services executed at site. | Part of Tender
| TOTAL FOR MISCELLANEOUS WORKS | [5 empty] | Rs. | 0

## GIANI FIRE BOQ
FIRE FIGHTING WORK BOQ
GIANI'S
S. No. | DESCRIPTION | UNIT | EXECUTED QTY | ANNEXURE RATE | ANNEXURE AMOUNT | TFS Rates | Material Rate | Labour Rate | Wastage | Rupees | Remark's | Final -Amount | Variation | EXCEEDED QTY | EXCEEDED AMOUNT
1 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 / 1239 for hydrent and sprinkler applications including fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, U bolt and including painting of two coats of Red Oxide , painting with two or more coats of synthetic enamel paint of Post office red shade complete as required.The installation includes all civil openings , breakages and making good the same. ( Final Quantity Measure as per site after working ) | [10 empty] | 0 | #VALUE!
1.1 | 25 mm dia | Mtr. | 7 | 430 | 3010 | 430 | [5 empty] | 3010 | 0
1.2 | 32 mm dia | Mtr. | [9 empty] | 0 | 0
1.3 | 40 mm dia | Mtr. | [9 empty] | 0 | 0
1.4 | 50 mm dia | Mtr. | [9 empty] | 0 | 0
1.5 | 65 mm dia | Mtr. | [9 empty] | 0 | 0
1.6 | 80 mm dia | Mtr. | [9 empty] | 0 | 0
1.7 | 100 mm dia | Mtr. | [9 empty] | 0 | 0
1.8 | 150 mm dia | Mtr. | [9 empty] | 0 | 0
1.9 | 200 mm dia, 6.0 mm thick | Mtr. | [9 empty] | 0 | 0
[12 empty] | 0 | 0
2 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 and 1239 for hydrent and sprinkler underground rings including all accessories such as screwed/ welded flanges, tees, reducers etc. Conforming to IS : 1239/3589 complete including , welding, jointing with compressed asbestos gaskets, nuts, bolts etc. as required. with cleaning, wrapping and coating of the pipe with 4 mm thick tar based plymaric corrosion protection tape or equivalent including applying uniform coat of cold pipekot primer as per IS; 10221 for protection against corrsion suitable for all kind of soil at 1.0 M depth including excavation and making good the same as required at site . ( Final Quantity Measure as per site after working ) | [10 empty] | 0 | 0
2.1 | 80 mm dia | Mtr. | [9 empty] | 0 | 0
2.2 | 100 mm dia | Mtr. | [9 empty] | 0 | 0
2.3 | 150 mm dia | Mtr. | [9 empty] | 0 | 0
[12 empty] | 0 | 0
3 | Supply, installation, testing and commissioning of Brass ball valves of following sizes as required. | [10 empty] | 0 | 0
3.1 | 25 mm dia. | Each | [9 empty] | 0 | 0
3.2 | 32 mm dia. | Each | [9 empty] | 0 | 0
3.3 | 40 mm dia. | Each | [9 empty] | 0 | 0
3.4 | 50 mm dia | Each | [9 empty] | 0 | 0
3.5 | 65mm dia. | Each | [9 empty] | 0 | 0
[12 empty] | 0 | 0
4 | Supply, fixing, testing & commissioning of 15 mm dia size ,quartzoid bulb sprinkler heads suitable for 68 degree centigrade rating of the following type : | [10 empty] | 0 | 0
4.1 | Pendant type | Each | 3 | 550 | 1650 | 470 | [5 empty] | 1410 | -240
4.2 | Upright type | Each | [9 empty] | 0 | 0
4.3 | Side wall type | Each | [9 empty] | 0 | 0
[12 empty] | 0 | 0
5 | Supply & Fixing ISI marked ( IS : 15683 ) Portable Fire Exitnguisher, ABC type,finished externally with red enamel paint, complete in all respects including initial fill and wall suspension of following capacity. | [10 empty] | 0 | 0
5.1 | 6 kg | Each | [9 empty] | 0 | 0
6 | Supply & Fixing ISI marked ( IS : 15683 ) Portable fire Extinguisher, Carbon‐dioxide type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill with C02 gas confirming to IS:307‐1966 filled to a filling ratio of not more than 0.667and wall suspension bracket. Capacity 5 Kg. | Each | [9 empty] | 0 | 0
7 | Supply & Fixing ISI marked ( IS : 15683 ) Portable fire Extinguisher, k type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill. Capacity 6kg | Each | [9 empty] | 0 | 0
8 | Supply and fixing M.S. structural work fabricated from standard sections i.e. rounds, solid angles, slotted angles, channels including cutting to size, drilling, welding, fixing and welding to insert plates in RCC structural members as directed by Engineer-in-charge including cutting and making good the walls and floors (for hangers, supports, clamps, etc.) | Kg | [9 empty] | 0 | 0
9 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required. | [10 empty] | 0 | 0
9.1 | 700 MM LONG | Each | [9 empty] | 0 | 0
|  |  | ANNEXURE AMOUNT-1 |  | 4660 |  | Grand Total |  |  |  |  | 4420 | #VALUE!

## GIANI FIRE JMS
S. No. | DESCRIPTION | UNIT | QTY | EXECUTED QTY | RATE | AMOUNT
1 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 / 1239 for hydrent and sprinkler applications including fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, U bolt and including painting of two coats of Red Oxide , painting with two or more coats of synthetic enamel paint of Post office red shade complete as required.The installation includes all civil openings , breakages and making good the same. ( Final Quantity Measure as per site after working )
1.1 | 25 mm dia | Mtr. | 7 | 7 | 430 | 3010 | OK
1.2 | 32 mm dia | Mtr. | 0 |  |  | 0
1.3 | 40 mm dia | Mtr. | 0 |  |  | 0
1.4 | 50 mm dia | Mtr. | 0 |  |  | 0
1.5 | 65 mm dia | Mtr. | 0 |  |  | 0
1.6 | 80 mm dia | Mtr. | 0 |  |  | 0
1.7 | 100 mm dia | Mtr. | 0 |  |  | 0
1.8 | 150 mm dia | Mtr. | 0 |  |  | 0
1.9 | 200 mm dia, 6.0 mm thick | Mtr. | 0 |  |  | 0
2 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 and 1239 for hydrent and sprinkler underground rings including all accessories such as screwed/ welded flanges, tees, reducers etc. Conforming to IS : 1239/3589 complete including , welding, jointing with compressed asbestos gaskets, nuts, bolts etc. as required. with cleaning, wrapping and coating of the pipe with 4 mm thick tar based plymaric corrosion protection tape or equivalent including applying uniform coat of cold pipekot primer as per IS; 10221 for protection against corrsion suitable for all kind of soil at 1.0 M depth including excavation and making good the same as required at site . ( Final Quantity Measure as per site after working )
2.1 | 80 mm dia | Mtr. | 0 |  |  | 0
2.2 | 100 mm dia | Mtr. | 0 |  |  | 0
2.3 | 150 mm dia | Mtr. | 0 |  |  | 0
3 | Supply, installation, testing and commissioning of Brass ball valves of following sizes as required.
3.1 | 25 mm dia. | Each | 1 |  |  | 0
3.2 | 32 mm dia. | Each | 0 |  |  | 0
3.3 | 40 mm dia. | Each | 0 |  |  | 0
3.4 | 50 mm dia | Each | 0 |  |  | 0
3.5 | 65mm dia. | Each | 0 |  |  | 0
4 | Supply, fixing, testing & commissioning of 15 mm dia size ,quartzoid bulb sprinkler heads suitable for 68 degree centigrade rating of the following type :
4.1 | Pendant type | Each | 2 | 3 |  | 0 | OK
4.2 | Upright type | Each | 0
4.3 | Side wall type | Each | 0 |  |  | 0
5 | Supply & Fixing ISI marked ( IS : 15683 ) Portable Fire Exitnguisher, ABC type,finished externally with red enamel paint, complete in all respects including initial fill and wall suspension of following capacity.
5.1 | 6 kg | Each | 1 |  |  | 0
6 | Supply & Fixing ISI marked ( IS : 15683 ) Portable fire Extinguisher, Carbon‐dioxide type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill with C02 gas confirming to IS:307‐1966 filled to a filling ratio of not more than 0.667and wall suspension bracket. Capacity 5 Kg. | Each | 1 |  |  | 0
7 | Supply & Fixing ISI marked ( IS : 15683 ) Portable fire Extinguisher, k type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill. Capacity 6kg | Each | 0
8 | Supply and fixing M.S. structural work fabricated from standard sections i.e. rounds, solid angles, slotted angles, channels including cutting to size, drilling, welding, fixing and welding to insert plates in RCC structural members as directed by Engineer-in-charge including cutting and making good the walls and floors (for hangers, supports, clamps, etc.) | Kg | 0 |  |  | 0
9 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required.
9.1 | 700 MM LONG | Each | 0 |  |  | 0