## HVAC
PROJECT : AMD, CIP LOUNGE AT T1
Date
S.NO | ITEM DESCRIPTION | UNIT | QTY. | Rate (INR) |  |  | Amount (INR) |  |  | QTY. | Rate (INR) |  |  | Amount (INR)
| SUB HEAD I - AIR-CONDITIONING SYSTEM |  |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
1.0 | EQUIPMENT
1.1 | FLOOR MOUNTED AIR HANDLING UNIT UVGI AND MERV-13
Supplying, installing, testing and commissioning of chilled water based double skin construction draw thru type Air Handling Unit (AHU) as per specification, each complete with following:
Inner skin of casing shall be constructed out of 24 gauge plain GS sheet & outer skin in 24 gauge pre-plasticized GS sheet sandwitched between 50mm thick injected PU foam insulation of density not less than 40 Kg /CuM and complete with inspection doors including control wiring as required. AHU shall have access for all parts
Fan section shall be complete with Plug fans. Fan should be suitable for VFD operation. All fans shall be AMCA certified.
Pre filter (MERV 8), 50mm thick washable synthetic fibre filter, face velocity not exceeding 500FPM. AHU shall be provided with MERV-13 filters (Bag type filter).
Six row deep cooling coil of copper tube, copper header and aluminum fins sized at maximum face velocity of 500 fpm. Cooling coil frame work and coil end plate shall be of SS304 construction. Wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge stainless steel duly insulated as per specifications.
Squirrel cage induction motors, IP-55, IE-3 suitable for 415 ± 10% volts, 50 Hz, AC supply meeting criterion as per ASHRAE standard 90.1-2013 and 90% or higher efficiency, suitable for VFD operation.
AHUs shall be complete with vibration isolation arrangement, rubber grooments etc to make installation vibration free.
Fan outlet velocity not exceeding 10.16 mps.
Total static pressure & motor rating shall be determined by contractor in co-ordination with manufacturer considering pressure drop across all accessories on supply air streams as per final appoved shop drawings.
Sound level at 1 m distance not exceeding 55 dB(A).
Starter panel for AHU and necessary electrical and control cables from starter panel to AHU shall be inclusive with AHU.
AHU shall be provided complete with doors to access the AHU parts. Contractor has to submit the AHU GA drawing showing piping connection side, door size, AHU size etc. Technical submittal for the same has to be approved from the consultants prior to procurement.
UVGI Specifications
AHU UVGI system with all accessories and framework required to mark fully functional in AHU’s for maintaining indoor Air Quality & Deep Coil Cleaning. Quantities of UVGI Lams shall be selected to cover entire cooling coil area with even distribution of light. The UVGI Equipment shall be listed to UL/CE Certified for electrical and fire & safety. UVGI system supplied must be in strict conformity with the specifications. The lamp shall have 9000 hrs. life, ballasts shall be electronic type, life rated greater > 14000 hrs. The UV system shall be installed on upstream side of cooling coil to avoid wind-chill effect. The UV emitters must be suitable for high airflow and low temperature operation. UV lamps should be operated in 254 nM wavelength, minimum intensity of UV light at surface of cooling coil shall be greater than 500 uW/cm2. UVGI system should be equipped with microprocessor-based control panel and shall have feature of run hour monitoring, Lamp fault Status, BMS compatibility. UVGI’s shall be suitable for following AHU Unit CFM.
AHU Capacity S.P Motor Rating Rows Area to be
No. (Cfm/TR) (mmWG) (HP) of coils fed
| AHU-1 20210/37TR 55 15 6 Lounge Area | No | 1 | 721050 | 114715 | 835765 | 721050 | 114715 | 835765 | 1 | 624797.43 | 104663.5 | 729460.93 | 624797.43 | 104663.5 | 729460.93
1.2 | VENTILATION FANS
1.2.1 | INLINE FANS WITHOUT FILTER
Supply, installation, testing and commissioning of duct mounted IN-LINE FANS for exhaust air as shown in drawings. Each fan shall be complete with motor, mounting flanges, accessories like bird screen, fixed louvers and GI sheet canopy for weather protection as required. Quoted price shall be inclusive of electronic speed regulator and wiring between fan & speed regulator for single phase fans. Incase of 3 phase fans quoted price shall be inclusive of DOL starter panel with cabling between starter panel and fan.
Quoted prices shall be inclusive of all necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling with painting with one coat of primer and two coats of paint to supports of MS work. In addition, 18G GI sheet canopy work and vibration isolator pads to make installation vibration free for fans to be installed on terrace.
| Fan Selection arrangement shall be as follows: |  |  |  |  | 0 | [6 empty] | 0
| Fan Capacity S.P Area to |  |  |  |  | 0 | [6 empty] | 0
| No. (Cfm) (mmWG) to be exhausted |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
a. | IF-1(Circular) 500 16-17 Toilets adjoing live display kitchen | No | 1 | 12017 | 3825 | 15842 | 12017 | 3825 | 15842 | 1 | 12000 | 3635 | 15635 | 12000 | 3635 | 15635
b. | IF-2(Rectangular) 1200 14-15 Male, Female and Disabled Toilet | No | 1 | 33320 | 4915 | 38235 | 33320 | 4915 | 38235 | 1 | 33000 | 4800 | 37800 | 33000 | 4800 | 37800
e. | IF-4(Circular) 1000 10-12 Live Display Kitchen | No | 1 | 31140 | 4915 | 36055 | 31140 | 4915 | 36055 | 1 | 31140 | 4915 | 36055 | 31140 | 4915 | 36055
| Contactor to check/calculate static pressure drop as per shop drawing. |  |  |  |  | 0 | [6 empty] | 0
| Note: Cigar Room Inline fan will be low noise type, sound level should not exceed 40dBA @ 2meters. Selection for the same to be done accordingly. |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
2.1 | CHILLED WATER PIPING |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Supply , Installation, Testing and Commissioning of MS heavy class (Class "C') pipes cut to requird lengths and installed with all welded joints. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers, sockets etc., and hanging arrangement and floor supports as required, rigid PUF saddles, washers and check nuts etc in accordance with the approved shop drawings and specifications. All sleeves in Fire wall/slab shall be sealed using fireproof sealant. Pipes shall be of following sizes : |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| For Pipe sizes of 80mm dia & above complete "C" channel support shall be provided. For floor supports, supports shall be complete with pipes of adequate size with base plate & vibration isolation pads and "C" channel. All pipe supports channels, fastner etc. to be selected as per support depth & loading as per structural consultant recommendations. |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
a. | 80mm dia | RM | 4 | 1912 | 600 | 2512 | 7648 | 2400 | 10048 | 4 | 1912 | 600 | 2512 | 7648 | 2400 | 10048