## HVAC
PROJECT : AMD, CIP LOUNGE AT T1
Date
S.NO | ITEM DESCRIPTION | UNIT | QTY. | Rate (INR) |  |  | Amount (INR) |  |  | QTY. | Rate (INR) |  |  | Amount (INR)
| SUB HEAD I - AIR-CONDITIONING SYSTEM |  |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
2.2 | CONDENSATE DRAIN PIPING -GI |  |  |  |  | 0 | [6 empty] | 0
| Supply, Installation , Testing and Commissioning |  |  |  |  | 0 | [6 empty] | 0
| of GI medium class (Class 'B') pipes cut to requird |  |  |  |  | 0 | [6 empty] | 0
| lengths and installed with all screwed joints |  |  |  |  | 0 | [6 empty] | 0
| for condensate drain. Quoted price |  |  |  |  | 0 | [6 empty] | 0
| shall be inclusive of supply and fixing in |  |  |  |  | 0 | [6 empty] | 0
| position the necessary fittings like elbows, tees |  |  |  |  | 0 | [6 empty] | 0
| reducers etc., and supporting arrangement |  |  |  |  | 0 | [6 empty] | 0
| in accordance with the approved shop drawings |  |  |  |  | 0 | [6 empty] | 0
| and specifications.Pipes shall be insulated with |  |  |  |  | 0 | [6 empty] | 0
| 9mm thick closed cell elastomeric insulation |  |  |  |  | 0 | [6 empty] | 0
| in tubing form . Pipes shall be of following sizes : |  |  |  |  | 0 | [6 empty] | 0
a. | 50mm dia | RM | 3 | 1205 | 395 | 1600 | 3615 | 1185 | 4800 | 3 | 1205 | 395 | 1600 | 3615 | 1185 | 4800
[6 empty] | 0 | [6 empty] | 0
3 | AIR DISTRIBUTION |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
3.1 | Supply, installation and testing of SITE Fabricated GI sheet metal ducts as per IS-655 Standard in accordance with the approved shop drawings as required by the specifications. Quoted price shall be inclusive of all necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and two coats of paint to supports of MS work. Quoted price shall be inclusive of scaffolding work as required. Note:All exposed surfaces & duct shall be painted in black mat finish by the HVAC contractor. |  |  |  |  | 0 | [6 empty] | 0
3.1.1 | 24 gauge galvanised sheet steel (0.63 mm) | Sqm. | 892 | 1147 | 437 | 1584 | 1023124 | 389804 | 1412928 | 892 | 1090 | 415 | 1505 | 972280 | 370180 | 1342460
3.1.2 | 22 gauge galvanised sheet steel (0.8 mm) | Sqm. | 345 | 1315 | 437 | 1752 | 453675 | 150765 | 604440 | 345 | 1250 | 415 | 1665 | 431250 | 143175 | 574425
3.1.3 | 20 gauge galvanised sheet steel (1.0 mm) | Sqm. | 60 | 1475 | 600 | 2075 | 88500 | 36000 | 124500 | 60 | 1401 | 570 | 1971 | 84060 | 34200 | 118260
3.1.4 | 18 gauge galvanised sheet steel (1.25 mm) | Sqm. | 60 | 1805 | 605 | 2410 | 108300 | 36300 | 144600 | 60 | 1715 | 575 | 2290 | 102900 | 34500 | 137400
[6 empty] | 0 | [6 empty] | 0
3.2 | Supply, Installation,Testing and Balancing of flexible ducting comprising of inner as well as outer skin constructed out of aluminium & fibre glass insulation 25mm thick of minimum 24 kg/cu.m density insulation sandwitched in between. Duct should confirm to fire rating standards BS-476 part 5, 6 & 7. Flexible Ducts of following sizes as per approved shop drawings, specifications : |  |  |  |  | 0 | [6 empty] | 0
3.2.1 | 350 mm dia. | Mtr. | RO | 805 | 173 | 978 |  |  |  | RO | 805 | 173 | 978
3.2.2 | 300 mm dia. | Mtr. | 35 | 655 | 165 | 820 | 22925 | 5775 | 28700 | 35 | 655 | 165 | 820 | 22925 | 5775 | 28700
3.2.3 | 200 mm dia. | Mtr. | 12 | 546 | 165 | 711 | 6552 | 1980 | 8532 | 12 | 546 | 165 | 711 | 6552 | 1980 | 8532
3.2.4 | 150 mm dia. | Mtr. | 12 | 495 | 140 | 635 | 5940 | 1680 | 7620 | 12 | 495 | 140 | 635 | 5940 | 1680 | 7620
3.2.5 | 100 mm dia. | Mtr. | 12 | 460 | 145 | 605 | 5520 | 1740 | 7260 | 12 | 460 | 145 | 605 | 5520 | 1740 | 7260
[6 empty] | 0 | [6 empty] | 0
3.3 | Supply, installation and testing of GI construction Opposed blade Volume control dampers within ducts to be provided with suitable ducts lever and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | Sqm. | 5 | 7975 | 1315 | 9290 | 39875 | 6575 | 46450 | 5 | 7975 | 1315 | 9290 | 39875 | 6575 | 46450
[6 empty] | 0 | [6 empty] | 0
3.4 | Supply, installation, testing and commissioning of Motorised combined smoke & fire damper complete with control panel, inter connecting wiring at locations shown in approved shop drawings and as per specifications. |  |  |  |  | 0 | [6 empty] | 0
3.4.1 | Smoke & Fire Dampers. | Sqm. | 5.5 | 26000 | 1315 | 27315 | 143000 | 7232.5 | 150232.5 | 5.5 | 24700 | 1250 | 25950 | 135850 | 6875 | 142725
3.4.2 | Control Panel & Wiring (including actuators) | No | 8 | 13656 | 2185 | 15841 | 109248 | 17480 | 126728 | 8 | 13656 | 2075 | 15731 | 109248 | 16600 | 125848
[6 empty] | 0 | [6 empty] | 0
3.5 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply Air Grilles with multiblade type key operated grille louver dampers in accordance with the approved shop drawings and specifications. | Sqm. | 7 | 12565 | 1095 | 13660 | 87955 | 7665 | 95620 | 7 | 12020 | 1095 | 13115 | 84140 | 7665 | 91805
[6 empty] | 0 | [6 empty] | 0
3.6 | Supply, installation, testing and balancing of powder coated extruded Aluminium Exhaust/Return Air Grilles without multiblade type grille louver dampers | Sqm. | 10 | 8195 | 1095 | 9290 | 81950 | 10950 | 92900 | 10 | 7785 | 1095 | 8880 | 77850 | 10950 | 88800
[6 empty] | 0 | [6 empty] | 0
3.7 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape Supply Air Diffusers with removable core & anti smudge ring & key operated volume control dampers as per approved drawings and specifications. | Sqm. | 3 | 14750 | 1640 | 16390 | 44250 | 4920 | 49170 | 3 | 14015 | 1640 | 15655 | 42045 | 4920 | 46965
[6 empty] | 0 | [6 empty] | 0
3.8 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape Return Air Diffusers as per approved drawings and specifications. | Sqm. | 3 | 12345 | 765 | 13110 | 37035 | 2295 | 39330 | 3 | 12350 | 765 | 13115 | 37050 | 2295 | 39345
[6 empty] | 0 | [6 empty] | 0
3.9 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction. Louvers with bird screen for exhaust air as per specifications and approved drawings. | Sqm. | 2.5 | 15625 | 765 | 16390 | 39062.5 | 1912.5 | 40975 | 2.5 | 14745 | 730 | 15475 | 36862.5 | 1825 | 38687.5
[6 empty] | 0 | [6 empty] | 0
3.1 | Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 6 | 1860 | 875 | 2735 | 11160 | 5250 | 16410 | 6 | 1860 | 875 | 2735 | 11160 | 5250 | 16410
[6 empty] | 0 | [6 empty] | 0
3.11 | Supply, Installation and Testing of single piece GI round spigot made out of spinning process with 50mm height and having grooves on both sides and circular flanges. Spigots shall be installed on main ducts to facilitate connection of flexible ducts. |  |  |  |  | 0 | [6 empty] | 0
3.11.2 | 300 mm dia. | Nos. | 35 | 985 | 440 | 1425 | 34475 | 15400 | 49875 | 35 | 985 | 440 | 1425 | 34475 | 15400 | 49875
3.11.3 | 200 mm dia. | Nos. | 12 | 875 | 440 | 1315 | 10500 | 5280 | 15780 | 12 | 875 | 440 | 1315 | 10500 | 5280 | 15780
3.11.4 | 150 mm dia. | Nos. | 12 | 765 | 330 | 1095 | 9180 | 3960 | 13140 | 12 | 765 | 330 | 1095 | 9180 | 3960 | 13140
3.11.5 | 100 mm dia. | Nos. | 12 | 765 | 330 | 1095 | 9180 | 3960 | 13140 | 12 | 765 | 330 | 1095 | 9180 | 3960 | 13140
[6 empty] | 0 | [6 empty] | 0
3.12 | Supply, Installation and Testing of Butterfly damper of aluminium sheet construction with two flap with sleeve as per thespecifications and shop drawings. |  |  |  |  | 0 | [6 empty] | 0
3.12.2 | 300 mm dia. | Nos. | 35 | 3060 | 440 | 3500 | 107100 | 15400 | 122500 | 35 | 2900 | 420 | 3320 | 101500 | 14700 | 116200
3.12.3 | 200 mm dia. | Nos. | 12 | 2625 | 440 | 3065 | 31500 | 5280 | 36780 | 12 | 2625 | 420 | 3045 | 31500 | 5040 | 36540
3.12.4 | 150 mm dia. | Nos. | 12 | 2405 | 330 | 2735 | 28860 | 3960 | 32820 | 12 | 2405 | 330 | 2735 | 28860 | 3960 | 32820
3.12.5 | 100 mm dia. | Nos. | 12 | 2075 | 330 | 2405 | 24900 | 3960 | 28860 | 12 | 2075 | 330 | 2405 | 24900 | 3960 | 28860
3.14 | THERMAL INSULATION
3.14.1 | THERMAL INSULATION FOR DUCTWORK
Supply and Application of external thermal insulation of supply /return air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Quoted price shall be inclusive of adhesive, tapes as per specification. insulation shall be provided with aluminium foil, factory laminated.
Insulation thickness/application will be as per approved shop drawing notes.
a. | 25 mm thick | Sqm | 25 | 1095 | 220 | 1315 | 27375 | 5500 | 32875 | 25 | 1095 | 220 | 1315 | 27375 | 5500 | 32875
c. | 16 mm thick | Sqm | 25 | 910 | 185 | 1095 | 22750 | 4625 | 27375 | 25 | 910 | 185 | 1095 | 22750 | 4625 | 27375
d. | 13 mm thick | Sqm | 875 | 820 | 165 | 985 | 717500 | 144375 | 861875 | 875 | 820 | 165 | 985 | 717500 | 144375 | 861875
e. | 9 mm thick | Sqm | 75 | 710 | 165 | 875 | 53250 | 12375 | 65625 | 75 | 710 | 165 | 875 | 53250 | 12375 | 65625
3.14.2 | ACOUSTIC LINING OF DUCTS
Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet.
a. | 10mm thick lining | SqM | 25 | 13495 | 165 | 13660 | 337375 | 4125 | 341500 | 25 | 13495 | 165 | 13660 | 337375 | 4125 | 341500
b. | 25mm thick lining | SqM | 120 | 1750 | 220 | 1970 | 210000 | 26400 | 236400 | 120 | 1750 | 220 | 1970 | 210000 | 26400 | 236400
3.14.3 | CHW PIPE INSULATION
Using Class 'O' Closed Cell Elastomeric Insulation
Supply and Application of 25mm/32mm thick closed cell elastomeric insulation in tubing form for chilled water piping as per the specifications. Quoted price shall be inclusive of adhesive as per specifications. Joints shall be sealed with adhesive forming proper bonding. Quoted price shall be inclusive of 24 G aluminium cladding for chilled water piping.
a. | 80mm dia (25mm thick) | RM | 10 | 1475 | 492 | 1967 | 14750 | 4920 | 19670 | 10 | 1475 | 492 | 1967 | 14750 | 4920 | 19670
3.15 | Air Transfer Grilles
| Supply, Installation and testing of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | 0.5 | 8050 | 1725 | 9775 | 4025 | 862.5 | 4887.5 | 0.5 | 8050 | 1725 | 9775 | 4025 | 862.5 | 4887.5
TOTAL ITEM NO. 3 (AIR DISTRIBUTION)
6 | AHU ROOM ACOUSTIC LINING |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Supply and Application of acoustic/ thermal lining of walls/ceiling of AHU rooms using resin bonded fibre glass insulation of density not less than 32Kg/CuM as per the approved shop drawings and specifications. Quoted price shall be inclusive of GSS channel, metal screws, washers, fibre glass tissue, perforated sheet etc. as required for complete installation. |  |  |  |  | 0 | [6 empty] | 0
a. | 50mm thick lining | SqM | 90 | 1915 | 495 | 2410 | 172350 | 44550 | 216900 | 90 | 1820 | 470 | 2290 | 163800 | 42300 | 206100
TOTAL ITEM NO. 6 (AHU ROOM ACOUSTIC LINING)