## HVAC
PROJECT : CIP LOUNGE AT T1
Date
S.NO | ITEM DESCRIPTION | UNIT | QTY. | Rate (INR) |  |  | Amount (INR) |  |  | QTY. | Rate (INR) |  |  | Amount (INR)
| SUB HEAD I - AIR-CONDITIONING SYSTEM |  |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
SUB HEAD II -KITCHEN VENTILATION SYSTEM (COOKING KITCHEN)
1.0 | EQUIPMENT
1.1.1 | Supplying, installing, testing and commissioning of Double Skin construction (of similar specification as that of AHU without mixing chamber and thermal break profile) Air Washer unit with DIDW class-I centrifugal fan (Efficiency >75%), TEFC weather proof motor of IP55 protection at 415±10% volts, 3 phase, 50 cycles power and high efficiency(IE3), belt drive, multisheave pulley mounted on motor and fan shaft, belt guard, motor and fan mounted on common base with metallistik vibration isolators. Fan capacity shall be based on outlet velocity not exceeding 10.16 MPS and fan speed not exceeding 1000 RPM. Total static pressure & Motor ratings shall be checked by Vendor/Contractor based on ducting layout.
Supplying, installing, testing and commissioning of horizontal monobloc pumps (1 W + 1 Standby) of suitable rating, of Beacon weir/KEC make factory mounted on GI channel base with electric motor for circulation of water. Pumps shall be aligned and suitable for 415±10% volts, 50 cycle’s 3 phase power supply. One No. 3 phase isolator switch in weather proof enclosure shall be provided near motor
In addition, quoted price shall be inclusive of civil work/channel etc. required to install FFU along with proper 18G GI sheet canopy work and vibration isolator pads to make installation vibration free, flexible canvass connection. Price shall be inclusive of bird screen at inlet.
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
| AW-1 7000 40-45 1.5 Kitchen Area | No | 1 | 437000 | 81940 | 518940 | 437000 | 81940 | 518940 | 1 | 400000 | 70000 | 470000 | 400000 | 70000 | 470000
1.1.2 | Supply , Installation , Testing and Commissioning of wet type scrubber (packaged type) comprising of following as per the specifications :
Fan section complete with backward curved DIDW type centrifugal fan/s, TEFC squirrel cage induction motor (IE3) suitable to operate on 415+10%V, 50Hz, 3 phase AC power supply and belt drive package. Casing of wet type scrubber shall be constructed out of 16 gauge GS sheet complete with inspection doors as required. Centrifugal fans shall be coated with epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS).
Wet section complete with double bank spray header in GI construction and nozzles, louvers PVC mist eliminators & mist collection tray made out of 16G GSS, strainer of fine mesh brass screen, globe valve, float valve, quick fill, over flow & drain connections, GI medium class piping and 3 phase monobloc pump of 0.5HP motor rating(1 W + 1 Standby) as required according to the capacity of scrubber machines. Wet section including sump will be made of 1.25mm thick SS-304 A grade stainless steel .
In addition, quoted price shall be inclusive of civil work/channel etc. required to install FFU along with proper 18G GI sheet canopy work and vibration isolator pads to make installation vibration free, flexible canvass connection.
The Scrubber Machines (EAC) shall be of following duty parameters :
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
| AS-1 7000 50 2 Kitchen Area | No | 1 | 1999275 | 131100 | 2130375 | 1999275 | 131100 | 2130375 | 1 | 1609401.08 | 120000 | 1729401.08 | 1609401.08 | 120000 | 1729401.08
| Note : Actual motor selection shall be done at manufacturer end. |  |  |  |  | 0 | [6 empty] | 0
| Contractor to calculate static pressure drop as per final installation within kitchen and approved shop drawing ductwork for Air Washer and Air-Scrubber |  |  |  |  | 0 | [6 empty] | 0
| TOTAL ITEM NO. 1 (EQUIPMENT) |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0