## FIREFIGHTING
PROJECT : CIP LOUNGE AT T1,
Date
S.NO | ITEM DESCRIPTION | UNIT | QTY. | Rate (INR) |  | Amount (INR)
D | SUB HEAD IV - FIRE DETECTION |  |  | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | TOTAL
Part III | FIREFIGHTING
D | SUB-HEAD IV-FIRE FIGHTING
42 | Supply, installation, testing and commissioning of following sizes of pipes conforming to IS-1239 with all accessories like all fittings ( all pipes & fittings upto 50mm dia threaded shall be the threaded Ductile Iron (ASTM A536) or Cast Iron (ASTM A126) or Forged Steel fittings and for pipes above 50 mm dia MS fitting with welded joint shall be used) including tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer including supporting/fixing the pipe on wall /ceiling with clamps, hangers (using anchor fastners) as per specification, Including synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager
MS pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwise and the supply of the same shall also be included in rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted.
For Sprinkler system - MS `C' Heavy class pipe
Ground Floor
| 25 mm dia | RM | 150 | 513 | 342 | 76950 | 51300 | 128250
| 40 mm dia | RM | 50 | 667 | 444 | 33350 | 22200 | 55550
| 50 mm dia | RM | 45 | 816 | 544 | 36720 | 24480 | 61200
| 65 mm dia | RM | 25 | 975 | 650 | 24375 | 16250 | 40625
| 80 mm dia | RM | 34 | 1285 | 855 | 43690 | 29070 | 72760
| 100 mm dia | RM | 20 | 1800 | 1195 | 36000 | 23900 | 59900
| 150 mm dia | RM | 70 | 2220 | 1500 | 155400 | 105000 | 260400
0
43 | Supply, installation, testing and commissioning of brass quartzoid sprinklers (UL approved) of 15 mm dia size, suitable for sustaining the pressure on the seat & water hammer effect. The type & temperature rating shall be as follows : | [6 empty] | 0
| Note : i)All sprinkler shall be chrome finish / powder coated. ii) Contractor shall ensure provision of sprinkler guard at no additional cost, as required by the Client. | [6 empty] | 0
0
| Horizontal side wall sprinkler - (68°C) sprinkler quick response | Nos. | 4 | 540 | 360 | 2160 | 1440 | 3600
0
45 | Providing and fixing fully charged ABC powder type (Mono-Ammonium Phosphate - MAP 90) portable fire extinguishers conforming to IS:15683, fixed to wall with brackets complete with initial charge. (Note: The cost for stand of fire extinguisher shall be included in this rate) | [6 empty] | 0
0
| Capacity 6 Kg. | Nos. | 2 | 1500 | 1000 | 3000 | 2000 | 5000
0
46 | Providing and fixing CO2 type cylindrical shape fire extinguisher with fixing hangers, hose, brackets, screws to required size etc.complete as per IS:15683:2006 - wall mounted type. | [6 empty] | 0
0
| Capacity 4.5 Kg. | Nos. | 2 | 4500 | 3000 | 9000 | 6000 | 15000
0
48 | Providing & fixing of butterfly valve (PN 16) with flanges, nut bolts, gaskets and necessary pad locking arrangement complete required. | [6 empty] | 0
0
| 150 mm dia | No. | 1 | 6180 | 4120 | 6180 | 4120 | 10300
0
50 | Supplying,fixing and commissioning of single headed internal hydrant valve with instantaneous Gunmetal/Stainless Steel coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Gunmetal/Stainless Steel cap and chain as required : Single headed Gunmetal :- | No. | 2 | 6410 | 4280 | 12820 | 8560 | 21380
0
51 | Supplying,fixing and commissioning of 63 mm dia, 30 m long RRL hose pipe with 63 mm dia male and female couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required : Gun Metal :- | Nos. | 4 | 5370 | 3570 | 21480 | 14280 | 35760
0
52 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 complete with the following as required. 20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS: 12585 20 mm nominal internal dia gun metal globe valve & nozzle. Drum and brackets for fixing the equipmets on wall. Connections from riser with 25 mm dia stop gun metal valve & M.S. Pipe and socket. 40 m :- | No. | 2 | 5585 | 3725 | 11170 | 7450 | 18620
[6 empty] | 0 | 0 | 0
53 | Supplying & fixing 63 mm dia gun metal short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required : Gun metal :- | No. | 2 | 3000 | 2000 | 6000 | 4000 | 10000
0
54 | Supply, installation, testing and commissioning of standard firemans axe with heavy rubber handle. | No. | 2 | 1410 | 940 | 2820 | 1880 | 4700
0
55 | Supply, installation, testing and commissioning of indoor type hose lockable cabinet frames fabricated from 2100 x 900 x 550mm(in front)/250mm(in back) angle iron sections and cabinet door is 550 mm with 1 SWG CRCA MS Sheets with full front thick rigid door (with MS frame) of size 2.1 m x 0.5m with centre opeaning and locking arrangement, suitable to accommodate landing valves, 15 m long hoses, first-aid hose reel, telephone, aler button, fire extinguishers and branch pipe nozzle & fire mans’ axe. The cabinet frame shall be painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade as required. The item shall be complete of MS housing with front door for the cabinet along with hammer. | No. | 2 | 15600 | 10400 | 31200 | 20800 | 52000 | `
| TOTAL SUB-HEAD IV carried over to Summary | [6 empty] | 855045