## Kitchen Ventilation
PROJECT : CIP LOUNGE AT T1,
Date
S.NO | ITEM DESCRIPTION | UNIT | QTY. | Rate (INR) |  |  | Amount (INR) |  |  | QTY. | Rate (INR) |  |  | Amount (INR)
|  |  |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
2 | AIR DISTRIBUTION |  |  |  |  | 0 | [6 empty] | 0
2.1 | Supply, installation and testing of SITE Fabricated GI sheet metal ducts as per IS-655 Standard in accordance with the approved shop drawings as required by the specifications. Quoted price shall be inclusive of all necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and two coats of paint to supports of MS work Note:All exposed surfaces & duct shall be painted in black mat finish by the HVAC contractor. |  |  |  |  | 0 | [6 empty] | 0
2.1.1 | 24 gauge galvanised sheet steel (0.63 mm) | Sqm. | 280 | 1150 | 440 | 1590 | 322000 | 123200 | 445200 | 280 | 1050 | 420 | 1470 | 294000 | 117600 | 411600
2.1.2 | 22 gauge galvanised sheet steel (0.8 mm) | Sqm. | 6 | 1295 | 440 | 1735 | 7770 | 2640 | 10410 | 6 | 1250 | 420 | 1670 | 7500 | 2520 | 10020
2.1.3 | 20 gauge galvanised sheet steel (1.0 mm) | Sqm. | 6 | 1475 | 605 | 2080 | 8850 | 3630 | 12480 | 6 | 1450 | 575 | 2025 | 8700 | 3450 | 12150
2.1.4 | 18 gauge galvanised sheet steel (1.25 mm) | Sqm. | 6 | 1805 | 605 | 2410 | 10830 | 3630 | 14460 | 6 | 1800 | 575 | 2375 | 10800 | 3450 | 14250
2.2 | Supply, installation and testing of GI construction Opposed blade Volume control dampers within ducts to be provided with suitable ducts lever and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | Sqm. | 1.5 | 7975 | 1315 | 9290 | 11962.5 | 1972.5 | 13935 | 1.5 | 7575 | 1315 | 8890 | 11362.5 | 1972.5 | 13335
2.3 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape Supply Air Diffusers with removable core & anti smudge ring & key operated volume control dampers as per approved drawings and specifications. | Sqm. | 1.5 | 14750 | 1640 | 16390 | 22125 | 2460 | 24585 | 1.5 | 14750 | 1640 | 16390 | 22125 | 2460 | 24585
2.4 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape Return Air Diffusers as per approved drawings and specifications. | Sqm. | 1.5 | 15625 | 765 | 16390 | 23437.5 | 1147.5 | 24585 | 1.5 | 15625 | 765 | 16390 | 23437.5 | 1147.5 | 24585
2.5 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction. Louvers with bird screen for exhaust air as per specifications and approved drawings. | Sqm. | 2 | 12020 | 1640 | 13660 | 24040 | 3280 | 27320 | 2 | 12020 | 1640 | 13660 | 24040 | 3280 | 27320
2.6 | Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 2.5 | 1955 | 920 | 2875 | 4887.5 | 2300 | 7187.5 | 2.5 | 1955 | 920 | 2875 | 4887.5 | 2300 | 7187.5
[6 empty] | 0 | [6 empty] | 0
2.7 | THERMAL INSULATION |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
2.7.1 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) |  |  |  |  | 0 | [6 empty] | 0
| (Using Factory Laminated fibre glass insulation) |  |  |  |  | 0 | [6 empty] | 0
| Supply and Application of external thermal insulation of ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg/CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. |  |  |  |  | 0 | [6 empty] | 0
b. | 50mm thick | SqM | 80 | 1420 | 450 | 1870 | 113600 | 36000 | 149600 | 80 | 1300 | 400 | 1700 | 104000 | 32000 | 136000
[6 empty] | 0 | [6 empty] | 0
2.7.3 | THERMAL INSULATION FOR EXPOSED DUCTS-AIR WASHER DUCT |  |  |  |  | 0 | [6 empty] | 0
| Supply and Application of external thermal insulation of supply air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Quoted price shall be inclusive of adhesive, tapes as per specification. insulation shall be provided with necessary glass cloth & UV protection paint for ducts exposed to atmosphere as per specifications. |  |  |  |  | 0 | [6 empty] | 0
a. | 25 mm thick | Sqm | 35 | 1150 | 385 | 1535 | 40250 | 13475 | 53725 | 35 | 1095 | 385 | 1480 | 38325 | 13475 | 51800
2.7.4 | THERMAL INSULATION FOR DUCTWORK-AIR WASHER DUCT IN AC AREA
Supply and Application of external thermal insulation of supply /return air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Quoted price shall be inclusive of adhesive, tapes as per specification. insulation shall be provided with aluminium foil, factory laminated.
a. | 25 mm thick | Sqm | 90 | 1150 | 385 | 1535 | 103500 | 34650 | 138150 | 90 | 1095 | 365 | 1460 | 98550 | 32850 | 131400
TOTAL ITEM NO. 2 (AIR DISTRIBUTION)
| TOTAL SUB-HEAD II carried over to Summary | [7 empty] | 3570952.5 | [6 empty] | 3063633.58