## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
B | AC PIPING
HVAC CONDENSATE DRAIN PIPE
B.1 | Supply and fixing in position of Rigid PVC condensate drain water piping with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. (Make: Astral, Supreme or equivalent with airport approval).
B.1.1 | 25 mm Ø | Mtr | 6
B.1.2 | 32 mm Ø | Mtr | 16
HVAC CHILLED WATER PIPING
B.2 | Supply, installation and testing of insulated chilled water piping with 26G aluminium cladding, necessary clamps, vibration isolators and fittings complete with all accessories like, shoe joints, bends, 'T'ees, reducers, expansion joints, supports, clamps, etc, duly insulated with EPS (Expanded Polystyrene) sections having density 24 Kg/M3 and thickness of 32 mm for pipes up to 50 mm dia,with vapor barrier covering and finished with protective coating(Pidilite/Equivalent) over a layer of glass cloth/canvas cloth for mechanical protection (Make: Jindal (Hissar), Tata Steel, SAIL or equivalent with airport approval).
B.2.1 | 40 mm Ø (Insulation thickness - 32 mm) | Mtr | 25
B.2.2 | 32 mm Ø (Insulation thickness - 32 mm) | Mtr | 20
B.3 | Supply, Installation, Testing, and Commissioning of Pressure Independent Control Valve (PICV) with Electric actuators with selectable control modes, with a pressure rating of PN 16 of approved make with threaded or flange connection ends with all necessary fixing arrangements. (Make: Danfoss,Siemen,Flowcon,Honeywell,Anergy,Belimo,Johnsons Control )
B.3.1 | 40 mm Ø (16.8 gpm) | Nos | 1
B.3.2 | 32 mm Ø (9.6 gpm) | Nos | 1
B.4 | Supply, Installation, Testing, and Commissioning of Forged Brass Y - Strainer with removable perforated SS mesh screen with a pressure rating of PN 16 of approved make, insulation shall be same thickness for corresponding size as chilled water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make: Emerald, Rapidcool or equivalent with airport approval).
B.4.1 | 40 mm Ø | Nos | 1
B.4.2 | 32 mm Ø | Nos | 1
B.5 | Supply, Installation, Testing, and Commissioning of Forged Brass Ball Valve with full bore lever operated with a pressure rating of PN 16 of approved make, Valve insulation shall be same thickness for corresponding size as chilled water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make: Rapidcool, RB, Emerald, Sant, Zoloto.)
B.5.1 | 40 mm Ø | Nos | 3
B.5.2 | 32 mm Ø | Nos | 3
B.6 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements. (Make: H.Guru, Fiebig, Emerald.)
B.6.1 | 100 mm Ø Dial | Nos | 4
B.7 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements. (Make: H.Guru, Fiebig, Emerald.)
B.7.1 | 100 mm Ø Dial | Nos | 4
C | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
C.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 56
C.1.2 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.Mtr | 110
C.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct | Sq.Mtr | 116
D | AIR DISTRIBUTION DUCT INSULATION & LINNING
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
D.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.1.1 | 19 mm thicknesses - (SAD) - Duct Insulation | Sq.Mtr | 56
D.1.2 | 19 mm thicknesses - (MUAD) - Duct Insulation | Sq.Mtr | 110
D.2 | Supply, installation & testing of Thermal Insulation of ducting using glass wool with silver foil covering, density 40 Kg/m3, Thermal Conductivity λ - 0.030 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.2.1 | 80 mm thicknesses - (KED) - Duct Insulation | Sq.Mtr | 116
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
D.3 | Supply, installation & testing of Acoustic Insulation of ducts using opencell processed elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.045 W/(m-K) at 0° C and Fire performance according to building regulations - Class 1 as per BS 476, with very good sound absorption, damping and barrier properties. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.3.1 | 15 mm thicknesses - (SAD) | Sq.Mtr | 5
E | AIR DISTRIBUTION DUCT ACCESSORIES
DUCT AIR CONTROL DAMPERS
D.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
D.1.1 | Size - 500 x 250 mm | Nos | 1
D.1.2 | Size - 400 x 150 mm | Nos | 1
D.1.3 | Size - 550 x 300 mm | Nos | 2
D.1.4 | Size - 550 x 250 mm MS FLANGE | Nos | 1
D.1.5 | Size - 400 x 150 mm MS FLANGE | Nos | 1
E | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Double Deflection Grille with opposed blade collar damper aerofoil adjustable blades with of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.1.1 | Neck Size - 450 x 450 mm | Nos | 6
E.1.1 | Neck Size - 300 x 300 mm | Nos | 1
E.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Double Deflection Grille with opposed blade collar damper aerofoil adjustable front and rear blades with collar damper frame of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.2.1 | Neck Size - 1000 x 400 mm | Nos | 1
E.2.2 | Neck Size - 5200 x 150 mm without damper | Nos | 3
E.3 | Supply, installation, tetsing and commissioning of Extruded Aluminium Single Deflection Grille with opposed blade collar damper aerofoil adjustable front and rear blades with collar damper frame of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.3.1 | Neck Size - 750 x 150 mm | Nos | 10
E.3 | Supply, installation, tetsing and commissioning of Extruded Aluminium Egg Crate Grille with collar damper 12.5 x 12.5 mm grid and 20 mm flange with collar damper Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements.
E.3.1 | Neck Size - 400 x 400 mm | Nos | 3
E.3.2 | Neck Size - 400 x 400 mm without damper | Nos | 3
F | TESTING & COMMISIONING
F.1 | Air Balancing & Chilled Water Testing & Commisioning | Lot | 1