## HVAC
BILL OF QUANTITIES
PROJECT: | ULAVACHARU_HYDERABAD AIRPORT |  |  | DATE: | 2024-03-11
|  |  |  | REV: | R0
HVAC SERVICES - WORKS BILL OF QUANTITIES |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | HVAC SYSTEM EQUIPMENTS
HVAC EQUIPMENTS
A.1 | Supply, Installation, Testing, and Commissioning of Chilled water type Double Skin Ceiling Suspended Air Handling Unit (AHU) of approved make with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment.Quote shall be inclusive of flexible connector ,Dielectric union & drain valve. (Make: Waves, System Air, Daikin, Voltas, Caryaire,Blue Star or equivalent with airport approval)
A.1.1 | 7.0 TR, 2100 CFM | Nos | 1
A.2 | Supply, Installation, Testing, and Commissioning of Chilled water type Double skin Medium static Fan Coil Unit (FCU) of approved make with all necessary standard pipe valves and accessories package kit as required for the selected equipment, with the option to controll the PICV and actuator via thermostat, with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. (Make: Waves, System Air, Daikin, Voltas, Caryaire,Blue Star or equivalent with airport approval)
A.2.1 | 4.0 TR, 1600 CFM | Nos | 1
KITCHEN EQUIPMENTS
A.3 | Supply, installation, testing, commissioning and field performance of ceiling suspended Electrostatic Precipitator (for removal of Kitchen Grease and Smoke particles) with all necessary supports and fittings. (Make: Rydair, Trion or equivalent with airport approval).
A.3.1 | 5000 CFM | Nos | 1
A.3.2 | 2300 CFM | Nos | 1
B | AC PIPING
HVAC CONDENSATE DRAIN PIPE
B.1 | Supply and fixing in position of Rigid PVC condensate drain water piping with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. (Make: Astral, Supreme or equivalent with airport approval).
B.1.1 | 25 mm Ø | Mtr | 6
B.1.2 | 32 mm Ø | Mtr | 16
HVAC CHILLED WATER PIPING
B.2 | Supply, installation and testing of insulated chilled water piping with 26G aluminium cladding, necessary clamps, vibration isolators and fittings complete with all accessories like, shoe joints, bends, 'T'ees, reducers, expansion joints, supports, clamps, etc, duly insulated with EPS (Expanded Polystyrene) sections having density 24 Kg/M3 and thickness of 32 mm for pipes up to 50 mm dia,with vapor barrier covering and finished with protective coating(Pidilite/Equivalent) over a layer of glass cloth/canvas cloth for mechanical protection (Make: Jindal (Hissar), Tata Steel, SAIL or equivalent with airport approval).
B.2.1 | 40 mm Ø (Insulation thickness - 32 mm) | Mtr | 25
B.2.2 | 32 mm Ø (Insulation thickness - 32 mm) | Mtr | 20
B.3 | Supply, Installation, Testing, and Commissioning of Pressure Independent Control Valve (PICV) with Electric actuators with selectable control modes, with a pressure rating of PN 16 of approved make with threaded or flange connection ends with all necessary fixing arrangements. (Make: Danfoss,Siemen,Flowcon,Honeywell,Anergy,Belimo,Johnsons Control )
B.3.1 | 40 mm Ø (16.8 gpm) | Nos | 1
B.3.2 | 32 mm Ø (9.6 gpm) | Nos | 1
B.4 | Supply, Installation, Testing, and Commissioning of Forged Brass Y - Strainer with removable perforated SS mesh screen with a pressure rating of PN 16 of approved make, insulation shall be same thickness for corresponding size as chilled water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make: Emerald, Rapidcool or equivalent with airport approval).
B.4.1 | 40 mm Ø | Nos | 1
B.4.2 | 32 mm Ø | Nos | 1
B.5 | Supply, Installation, Testing, and Commissioning of Forged Brass Ball Valve with full bore lever operated with a pressure rating of PN 16 of approved make, Valve insulation shall be same thickness for corresponding size as chilled water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make: Rapidcool, RB, Emerald, Sant, Zoloto.)
B.5.1 | 40 mm Ø | Nos | 3
B.5.2 | 32 mm Ø | Nos | 3
B.6 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements. (Make: H.Guru, Fiebig, Emerald.)
B.6.1 | 100 mm Ø Dial | Nos | 4
B.7 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements. (Make: H.Guru, Fiebig, Emerald.)
B.7.1 | 100 mm Ø Dial | Nos | 4
C | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
C.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 56
C.1.2 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.Mtr | 110
C.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct | Sq.Mtr | 116
D | AIR DISTRIBUTION DUCT INSULATION & LINNING
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
D.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.1.1 | 19 mm thicknesses - (SAD) - Duct Insulation | Sq.Mtr | 56
D.1.2 | 19 mm thicknesses - (MUAD) - Duct Insulation | Sq.Mtr | 110
D.2 | Supply, installation & testing of Thermal Insulation of ducting using glass wool with silver foil covering, density 40 Kg/m3, Thermal Conductivity λ - 0.030 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.2.1 | 80 mm thicknesses - (KED) - Duct Insulation | Sq.Mtr | 116
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
D.3 | Supply, installation & testing of Acoustic Insulation of ducts using opencell processed elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.045 W/(m-K) at 0° C and Fire performance according to building regulations - Class 1 as per BS 476, with very good sound absorption, damping and barrier properties. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.3.1 | 15 mm thicknesses - (SAD) | Sq.Mtr | 5
E | AIR DISTRIBUTION DUCT ACCESSORIES
DUCT AIR CONTROL DAMPERS
D.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
D.1.1 | Size - 500 x 250 mm | Nos | 1
D.1.2 | Size - 400 x 150 mm | Nos | 1
D.1.3 | Size - 550 x 300 mm | Nos | 2
D.1.4 | Size - 550 x 250 mm MS FLANGE | Nos | 1
D.1.5 | Size - 400 x 150 mm MS FLANGE | Nos | 1
E | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Double Deflection Grille with opposed blade collar damper aerofoil adjustable blades with of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.1.1 | Neck Size - 450 x 450 mm | Nos | 6
E.1.1 | Neck Size - 300 x 300 mm | Nos | 1
E.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Double Deflection Grille with opposed blade collar damper aerofoil adjustable front and rear blades with collar damper frame of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.2.1 | Neck Size - 1000 x 400 mm | Nos | 1
E.2.2 | Neck Size - 5200 x 150 mm without damper | Nos | 3
E.3 | Supply, installation, tetsing and commissioning of Extruded Aluminium Single Deflection Grille with opposed blade collar damper aerofoil adjustable front and rear blades with collar damper frame of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
E.3.1 | Neck Size - 750 x 150 mm | Nos | 10
E.3 | Supply, installation, tetsing and commissioning of Extruded Aluminium Egg Crate Grille with collar damper 12.5 x 12.5 mm grid and 20 mm flange with collar damper Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements.
E.3.1 | Neck Size - 400 x 400 mm | Nos | 3
E.3.2 | Neck Size - 400 x 400 mm without damper | Nos | 3
F | TESTING & COMMISIONING
F.1 | Air Balancing & Chilled Water Testing & Commisioning | Lot | 1
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## ELEC
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | ULAVACHARU_HYDERABAD AIRPORT |  |  | DATE: | 2024-03-11
|  |  |  | REV: | R0
ELECTRICAL SERVICES, CCTV & DATA - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
Item Code | Item Name | UOM | Qty | UNIT COST | REMARKS
A | METER / METER PANEL
A.1 | Supply, Installation, Testing & Commissioning of kWH / MFM Energy Meter Panel complete with Enclosure (If required as per site condition / Airport TDM). Energy Meter shall be of Digital kVAH Type and Make / Manufacturer from below list, or any other make with kVAH option with Approval from TS Department. For Make refer list below, Single Phase (For load below 40A) : Make - MID (Algodue Electronica), Model - UEM 40-2C. Type - Direct. Three Phase (For load below 60A) : Make - Secure, Model - Sprint 350, Type - Direct. Three Phase (For load above 60A) : 1) Make - Secure, Model - Elite 445, Type - C.T. 2) Make - Conzerv (Schneider Electric), Model - EM6438, Type - C.T. 3) Make - L & T, Model - Vega TM (WDM303FDWA1), Type - C.T.
A.1.1 | 125A/5A ENERGY METER (CT TYPE) | Nos. | 1
A.1.2 | 100A/5A ENERGY METER (CT TYPE) | Nos. | 1
B | LV CABLING
B.1 | Supply, Installation, Testing & Commissioning of Fire Rated LS/LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape / Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD / Load Calculation Sheet (Main Cable) & Unarmoured Single Core Wire (ECC), complete with Termination of the same with Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground / on Cable Tray / through Cable Trunking / in Pipe / on Wall / Trench as required. Make : Electrical Wires & Cables : Finolex, Polycab, RR Kables, KEI or equivalent. For cables laid on Cable Tray / in Pipe / on Wall / Trench - the rate shall include necessary supporting / clamping arrangements.
B.1.1 | 4C x 35 SQ.MM | Mtr. | 10
B.1.2 | 4C x 25 SQ.MM | Mtr. | 20
B.1.3 | 4C x 6 SQ.MM | Mtr. | 20
B.1.4 | 4C x 4 SQ.MM | Mtr. | 20
B.1.5 | 1C x 25 SQ.MM | Mtr. | 10
B.1.6 | 1C x 16 SQ.MM | Mtr. | 20
B.1.7 | 1C x 6 SQ.MM | Mtr. | 20
B.1.8 | 1C x 4 SQ.MM | Mtr. | 20
C | DISTRIBUTION BOARDS
C.1 | Supply, Installation, Testing & Commissioning of Surface / Flush mounting 10kA / 25kA (As per Panel requirement) Distribution Boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate & knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring & earth bus on insulation mount. Make : Electrical Panel / DB's & Breakers (MCB, RCBO, ELCB & MCCB) : Legrand, Siemens, ABB, Schneider or equivalent. All DB's must named as per the SLD / Load Calculation Sheet. Laminated SLD & Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB / RCBO shall be Hpi / Si series & MCB's shall be 'B" / 'C' Curve (As per requirement).
SMDB
C.1.1 | 10Way TPN Panel Board with 125A 4P MCCB incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
LPDB
C.1.2 | 18Way TPN Panel Board with 100A 30 mA 4 P RCBO incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
UPS DB
C.1.3 | 6 Way SPN Panel Board with 20A 30 mA 2P RCBO incomer and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
D | LIGHT FIXTURES POINT WIRING
D.1 | Supply, Installation, Testing & Commissioning of Light Fixture Point wiring (Light Fixtures to be as approved by Architect Design & BOQ) with Lamps, Ballasts / Drivers / Starters, Switches / Lighting Control Switch Board with Fire Rated LS/LSZH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Light Fixtures : Philips, Wipro, Crompton, Syska or equivalent. Make : PVC Conduits : Sudhakar, Shakti or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
D.1.1 | PENDANT LIGHT-01 (Point Wiring only) | Nos. | 14
D.1.2 | PENDANT LIGHT-02 (Point Wiring only) | Nos. | 27
D.1.3 | PENDANT LIGHT-03 (Point Wiring only) | Nos. | 4
D.1.4 | RECESSED DOWN LIGHT (Point Wiring only) | Nos. | 33
D.1.5 | LED PANEL LIGHT (600X600MM) (Point Wiring only) | Nos. | 11
D.1.6 | LED STRIP LIGHT WITH DIFFUSER(Point Wiring only) | Nos. | 1
D.1.7 | INDICATIVE SIGNAGE (Point Wiring only) | Nos. | 5
D.1.8 | Lighting Control Switch board with switches as required (Point Wiring only) | Nos. | 2
D.1.9 | EXIT LIGHT (Wall / Ceiling Mounted) | Nos. | 5
E | WIRING DEVICES (SWITCHES & SOCKETS)
E.1 | Supply, Installation, Testing & Commissioning of Wiring Devices (Switches & Sockets - Face Plate Finish as approved by Architect / Matching to Architecture Finishes) with Fire Rated LS/LSZH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Switch & Sockets : Anchor Roma / Penta, Legrand, Havells Crabtree, Finolex, L & T Switchgear or equivalent. Make : PVC Conduits : Sudhakar, Shakti or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
E.1.1 | 13A SINGLE SWITCHED SOCKET OUTLET | Nos. | 21
E.1.2 | 13A DUAL SWITCHED SOCKET OUTLET | Nos. | 3
E.1.3 | 13A SINGLE SWITCHED SOCKET OUTLET + USB PORT | Nos. | 4
E.1.4 | 13A DUAL SWITCHED SOCKET OUTLET + DUAL USB PORT | Nos. | 17
E.1.5 | 16A SINGLE SWITCHED SOCKET OUTLET | Nos. | 14
E.1.6 | 16A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET (3 PIN) (WALL MOUNTED) | Nos. | 4
E.1.7 | 16A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 2
E.1.8 | 16A DOUBLE POLE SWITCH WITH NEON INDICATOR | Nos. | 2
E.1.9 | 20A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 4
E.1.10 | 20A DOUBLE POLE SWITCH WITH NEON INDICATOR | Nos. | 4
E.1.11 | 20A SINGLE SWITCHED SOCKET OUTLET | Nos. | 4
E.1.12 | 20A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET (3 PIN) (WALL MOUNTED) | Nos. | 13
E.1.13 | 20A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 4
E.1.14 | 32A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 1
E.1.15 | 20A THREE PHASE ISOLATOR | Nos. | 1
F | CONTAINMENT (CABLE TRAY & TRUNKING)
F.1 | Supply & Installation of GI Cable Tray & GI Cable Trunking, through Wall / Ceiling / Floor as per drawings, complete with standard accessories / factory made fittings, earthing throughout the run with copper braids, wall / ceiling suspended supports, etc. Make : Cable Management System : Dudhat, Super, K.R. Power supports or equivalent with Airport approval.
F.1.1 | 75 x 75 MM CABLE TRUNKING | Mtr. | 9
F.1.2 | 50 x 50 MM CABLE TRUNKING | Mtr. | 24
G | UPS SYSTEM
G.1 | Supply, Installation, Testing & Commissioning of UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) & standard accessories / equipments required for complete functioning of the system, earthing, support system (if required), etc. Make : UPS System : Luminous, APC, Microtek or equivalent with Airport approval.
G.1.1 | 2 KVA Single phase UPS with 30 Minute Back-up | Nos. | 1
H | CCTV SYSTEM
H.1 | Supply, Installation, Testing & Commissioning of CCTV System with suitable / required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console / DVR, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make : CCTV System : Hikvision, Honeywell, Dahua, or equivalent with Airport approval. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
H.1.1 | CCTV Dome Camera, 4 Megapixel / As approved or confirmed by client, Real Day / Night, Exir, IR LED, IP 67, with all neccessary accessories, Power supply units etc. | Nos. | 7
H.1.2 | CCTV IP Dome Camera (CAT 6), 4 Megapixel / As approved or confirmed by client, Real Day / Night, Exir, IR LED, IP 67 with all neccessary accessories, Power supply units etc. | Nos. | 1
H.1.3 | DVR with 45 Days Back-up | Nos. | 1
I | DATA NETWORK SYSTEM
I.1 | Supply, Installation, Testing & Commissioning of Data & Telephone Network System with required cabling through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make : IT Cables & Accessories : Belden (Part Code - 7834ANC). The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
I.1.1 | Dual Data outlet (RJ45) Jack | Nos. | 3
I.1.2 | Single Data outlet (RJ45) | Nos. | 5
I.1.3 | Patch Cords (1.5 meters length) | Nos. | 11
GRAND TOTAL NET
NOTE : The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## PHE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | ULAVACHARU_HYDERABAD AIRPORT |  |  | DATE: | 2024-03-11
|  |  |  | REV: | R0
PLUMBING SYSTEM - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | DRAINAGE SYSTEM
INTERCEPTORS & SEPERATORS
A.1 | Supplying, Installing, Testing & Commissioning of Greese Trap or Grease Interceptor (Above Ground / floor) of 304 grade stainless steel material with interceptor body, preforated bucket, baffles, integral trap, inlet & outlep pipe sleeve and stainless steel interceptor cover of approved make and with all necessary fittings & connectors etc. (Make : Nugreen , Kessel and Concessionaire can propose another make in SS material.)
A.1.1 | NGT 30 - Flow Rate (0.95 LPS / 57 LPM) | Nos | 2
VALVES & ACCESSORIES
A.2 | Supplying, Installing, Testing & Commissioning of ABS Air Admittance Valve conforming to EN 12380, with an air admittance air flow rate of 6.1 L/s and a temperature range of operation from -20 C to + 60 C of approved make with all necessary adapters, fittings and connectors etc. (Make : Astral/Supreme for Pipe and Fittings)
A.2.1 | 32 mm Dia | Nos | 2
DRAINS, TRAPS & CLEANOUTS
A.3 | Supplying, Installing, and testing of AISI 304 grade Stainless Steel Floor Drain with top square anti-slip mesh grating drain cover of 2200 X 200 mm, lateral/horizontal outlet, with removable waste basket, odor water seal trap of approved make with all necessary adapters, fittings, and connectors etc. (Make : Custom made)
A.3.1 | 50 mm Dia - Outlet | Nos | 2
A.4 | Supplying, Installing, and testing of AISI 304 grade Stainless Steel Floor Drain with top square anti-slip mesh grating drain cover of 350 X 350 mm, lateral/horizontal outlet, with removable waste basket, odor water seal trap of approved make with all necessary adapters, fittings, and connectors etc. (Make : Custom made)
A.4.1 | 50 mm Dia - Outlet | Nos | 3
A.5 | Supplying, Installing, and testing of uPVC 'P' Trap (self-cleaning type) with odor water seal trap of approved make with all necessary adapters, fittings and connectors, etc.
A.5.1 | 32 mm Dia Outlet | Nos | 7
A.6 | Supplying, Installing & Testing of cast iron Floor Trap (150 mmx 150 mm) with Stainless Steel slotted top cover, odour water seal trap of approved make with all necessary adapters, fittings and connectors etc. (Makes : NECO or equivalent with Airport approval)
A.6.1 | 75 mm Dia - Outlet | Nos | 1
DRAINAGE SYSTEMS PIPING
A.7 | Supplying, Installing, Testing, and Commissioning of uPVC Pipe, for drainage with all necessary fittings such as bends, wye's, reducers, san tee's, double wye's, double combinations, san cross, and cleanout plugs etc, of approved make. and with all necessary supports/clamps for the above-raised floor pipes as per standards and site conditions/requirements. (Make : Astral/Supreme for Pipe and Fittings)
A.7.1 | 32 mm Dia | Mtr | 3
A.7.2 | 40 mm Dia | Mtr | 10
A.7.3 | 50 mm Dia | Mtr | 32
A.7.4 | 75 mm Dia | Mtr | 3
B | WATER SUPPLY SYSTEM
WATER SUPPLY EQUIPMENTS
B.1 | Supply, Installation, Testing & Commissioning of Electric Water Heater with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. and proper supports necessary as per standards and site condition / requirements. (Make : Crompton/Bajaj or equivalent with Airport approval)
B.1.1 | 30 Liters vertical storage water heater | Nos | 2
B.1.2 | 40 Liters vertical storage water heater | Nos | 1
B.2 | Supply, Installation, Testing & Commissioning of RO Filteration Unit for supplying pure filtered potable water to equipments like Combi-steamers & baking ovens, Fresh water taps & Coolers, Coffee/ Espresso machines, Dish-washers, Post-mix machines, Ice-machines, and Boiling-water taps etc. with necessary prefilters, filter cartridges, manifold heads, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. Final make, model and details to be finalized by specialist vendor after examining the water test report of incoming water supply provided at site. (Make : Eco Smart/Aquaguard or equivalent with Airport approval)
B.2.1 | 15 Ltrs / Hr - Flow Rate | Nos | 1
WATER SUPPLY PIPE VALVES & ACCESSORIES
B.3 | Supply, Installation, Testing & Commissioning of Brass Ball Valve with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar of approved make and with all necessary fittings. (Makes : NECO or equivalent with Airport approval)
B.3.1 | 15 mm Dia | Nos | 8
B.4 | Supply, Installation, Testing, and Commissioning of chrome plated Angle Valve with wall flange/rosette for all plumbing equipment/fixtures with a pressure rating of 16 Bar of approved make and with all necessary fittings. Including making good the wall/partition as per Architectural / Interior Design and as per relevant standards. (Makes : NECO or equivalent with Airport approval)
B.4.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 16
COLD WATER SUPPLY PIPING
B.5 | Supply, Installation, Testing & Commissioning of (Chlorinated Poly Vinyl Chloride) CPVC Pipe conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Astral/Supreme for Pipe and Fittings)
B.5.1 | 15 mm Dia | Mtr | 12
B.5.2 | 20 mm Dia | Mtr | 25
B.5.3 | 25 mm Dia | Mtr | 22
B.6 | Supply, Installation, Testing & Commissioning of Copper Pipe conforming to BS 2871 / EN 1057, (continous operating temperature range of maximum 90°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Manibhadra fittings or equivalent with Airport approval)
B.6.1 | 15 mm Dia | Mtr | 15
PIPING THERMAL INSULATION
B.7 | Supply & fixing of Pipe Insulation of 13 mm thick, with Polyethylene-based, closed-cell foam pipe insulation and polymer protective coating to prevent external mechanical damage of approved make for Hot water pipe with a operating temperature range of 0°C to 100°C, Thermal conductivity (λ) 0.038 W/m-K @ 40°C including suitable adhesives to fix the insulation to pipe. (Make : Thermax, Maxima, Fuelpac or equivalent)
B.7.1 | 15 mm Dia | Mtr | 15
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## FIRE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | ULAVACHARU_HYDERABAD AIRPORT |  |  | DATE: | 2024-03-11
|  |  |  | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
A.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangement with ceiling / wall etc. (Make: Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent with airport approval)
A.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 20
A.1.2 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 8
A.1.3 | Upright Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 28
FIRE SPRINKLER PIPE VALVES & ACCESSORIES
A.3 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.)
A.3.1 | 90 mm Dia | Nos | 1
A.4 | Supply, Installation, Testing & Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem & lever, with necessary weldable fittings in position as per drawings / site conditions. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.)
A.4.1 | 25 mm Dia | Nos | 1
A.5 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. (Make: Potter/ System Sensor or equivalent with airport approval)
A.5.1 | 90 mm Dia | Nos | 1
FIRE SPRINKLER PIPING
A.6 | Supply, Installation, Testing & Commissioning of MS "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) (Make: HSL, Mukut, Lalit steel or equivalent)
A.6.1 | 25 mm Dia | Mtr | 35
A.6.2 | 32 mm Dia | Mtr | 35
A.6.3 | 40 mm Dia | Mtr | 10
A.6.4 | 50 mm Dia | Mtr | 15
A.6.5 | 65 mm Dia | Mtr | 15
A.6.6 | 80 mm Dia | Mtr | 5
B | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE )
FIRE ALARM SYSTEM - DETECTION DEVICES
B.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke & Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles with all necessary mounting and fixing arrangements. (Above & Below Ceiling) Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.1.1 | Below ceiling level | Nos | 2
B.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles with all necessary mounting and fixing arrangements. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.2.1 | Heat Detector - 58°C fixed temperature | Nos | 1
B.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.3.1 | Manual Call Point - (Wall / Partition Mounted) | Nos | 1
B.4 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator & and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB / EN54 along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.4.1 | Sounder Strobe - (Wall / Partition Mounted) | Nos | 1
FIRE ALARM SYSTEM - MODULE DEVICES
B.5 | Supply, Installation, Testing, and Commissioning of Addressable Type Control Module for shutting down FCU’s, and magnetic fire door holders. Elevator recall, fire damper, pressurization fan, strobes etc along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.5.1 | Control Module | Nos | 1
B.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolation Module along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
B.6.1 | Isolation Module | Nos | 2
C | FIRE EXTINGUISHERS
C.1 | DRY POWDER STORED FIRE EXTINGUISHER
C.1.1 | Supply and fixing of 4.0 Kg ABC Dry Powder (Stored Pressure) Type Fire Extinguisher. pressurized with dry nitrogen gas at 15 bar. Design, construction and testing as per IS 15683 with BIS Fire rating 2A : 21B, Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 3
C.2 | CO2 PORTABLE FIRE EXTINGUISHER
C.2.1 | Supply and fixing of 3.0 Kg CO2 (Carbon-dioxide) Type Fire Extinguisher. Design, construction and testing as per IS 15683 with BIS Fire rating 21B, Body Hydrotested at 250 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 4
C.6 | FIRE EXTINGUISHER MOUNTING BRACKET / MOUNTING STAND
C.6.1 | Supply and fixing of Mounting Bracket / Stand for Fire Extinguishers fabricated out of good quality M.S, Pipe / Plate & Fittings duly painted with primer and final enamel paint coat as per the regulatory authority or to match with the ID design to suit the above Fire Extinguishers. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 7
GRANT TOTAL
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.