## FIRE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | ULAVACHARU_HYDERABAD AIRPORT |  |  | DATE: | 2024-03-11
|  |  |  | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
C | FIRE EXTINGUISHERS
C.1 | DRY POWDER STORED FIRE EXTINGUISHER
C.1.1 | Supply and fixing of 4.0 Kg ABC Dry Powder (Stored Pressure) Type Fire Extinguisher. pressurized with dry nitrogen gas at 15 bar. Design, construction and testing as per IS 15683 with BIS Fire rating 2A : 21B, Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 3
C.2 | CO2 PORTABLE FIRE EXTINGUISHER
C.2.1 | Supply and fixing of 3.0 Kg CO2 (Carbon-dioxide) Type Fire Extinguisher. Design, construction and testing as per IS 15683 with BIS Fire rating 21B, Body Hydrotested at 250 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 4
C.6 | FIRE EXTINGUISHER MOUNTING BRACKET / MOUNTING STAND
C.6.1 | Supply and fixing of Mounting Bracket / Stand for Fire Extinguishers fabricated out of good quality M.S, Pipe / Plate & Fittings duly painted with primer and final enamel paint coat as per the regulatory authority or to match with the ID design to suit the above Fire Extinguishers. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 7
GRANT TOTAL
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.