## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
Note: | Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | CHILLED WATER TYPE CASSETTE UNIT :
1.1 | CASSETTE UNIT with VALVE STATION
Supply, installation, testing and commisssiong of Cassette's complete with Centrifugal fan scroll, double blower section with split capacitor motor mounted on common shaft, synthetic filter with filter frame with easy removal facility, In-built drain pump, chilled water piping arrangement and finned 4 row cooling coil alongwith supporting threaded rods, nuts, bolts etc. Cassette unit must have extended / double drain pans to accommodate controls and valves.
All factory fitted valve connection such as Modulating type PIBCV valve, Brass Ball Valve and Brass Ball Valve with Strainer along with SS Mesh shall be provided along with unit. It shall include with Power wiring from the 5A switch socket within 2m along with a 5A plug top. Also, the cost shall include a Siemens / Honeywell make of wired remote controller to integrate with the BMS, along with 5m cabling.
Make : Midea / VTS / Daikin
a | Capacity: 1.0 TR | No. | 1
2 | CHILLED WATER PIPING WITH INSULATION:
2.1 | CHW PIPE
SITC of MS Heavy duty class 'C' ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker/ paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. "Table E" of BS code for flange thickness to be adhered.
Make: Jindal Hissar / TATA
a | Φ 25 mm | Rmt | 40
2.2 | CHILLED WATER PIPING INSULATION - INTERNAL
SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class "O" Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports. Finally sealing with 3M glass cloth vapour barrier.
Make: Armaflex & K-flex
a | Φ 25 mm | Rmt | 45
2.3 | BALL VALVE
SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure: Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
Make: Zoloto / Audco / Kitz
a | Φ 25 mm | Nos. | 2
2.4 | INSULATED CONDENSATE DRAIN PIPE
SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees & reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
Make: Supreme, Prince, Astral
a | Φ 25 mm | Rmt | 10
2.5 | BTU METER
Supply, installation, testing & fixing in position of BTU meter with all fittings and accessories in chilled water pipe line of the following sizes. Meter to be installed along with isolating valve and suitable strainer as specified by the manufacturer.
Make: Johnson, Honeywell, Siemens, Sauter, Kamstrup
a | Φ 25 mm | Nos. | 1
NOTES FOR PIPING:
a | Cover all open pipe ends with muslin cloth during construction
b | Pipe cleaning & chemical treatment as per specs shall be included in the piping cost.
c | Unit rates for all indicated sizes of pipes & valves shall be furnished.
d | Cleaning/Painting of pipe before insulation shall be included in piping cost.
e | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant.
f | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
3 | VENTILATION SYSTEM:
3.1 | KITCHEN DRY SCRUBBER
SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% & units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
Finishing - Power coated, Dark Blue
Operating voltage - 220 Vac+/-10%, 50 Hz (Single phase)
Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator
Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
Particle Size - Collects particles as small as 0.01 microns
Motor - Sealead ball bearings UL, single phase.
Cell - Ionizing voltage - 12 KVdc
Collector voltage - 6 KVdc
One cell comprising of 9 ionizing wires and 25 collection plates
Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
Pre-filter - Aluminium mesh, washable Dry contact for BMS.
Make: Rydair / Espair
a | CFM - 4000 | Nos. | 1
4 | SHEET METAL WORKS:
4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. All ducts has to be powder coated by HVAC contractor, sample and color code to be presented for the validation of Client / Architect.
GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
a | 18 Gauge GI Sheet Metal Duct (Above 2251mm & Plenum) | Sq.mtr |  |  | RO
b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) | Sq.mtr |  |  | RO
c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr |  |  | RO
d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 220
4.2 | EXTRUDED ALUMINIUM CEILING GRILLES
SITC of Aluminium extruded powder coated Supply & Return air Linear grilles with four side flanges,etc.
Make: Cosmos, Air Master & System Air
a | Linear / Square / Rectangular Grille | Sq.mtr | 1.5
4.3 | EXTRUDED ALUMINIUM LOUVER with BIRD SCREEN
| SITC of Aluminium extruded powder coated Louver with four side flanges, wire mesh bird screen etc. | Sq.mtr |  |  | RO
Make: Cosmos, Air Master & System Air
4.4 | SS EXHAUST AND FRESH AIR GRILLES FOR KITCHEN
SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature.
Make: Carryaire / System Air / Dynacraft / Air Master
a | Linear / Square / Rectangular Grille | Sq.mtr | 1
4.5 | OPPOSED BLADE DAMPER
| SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 2.5
Make: Cosmos, Air Master & System Air
4.6 | MULTI LEAF VOLUME CONTROL DAMPER
| SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 1
Make: Cosmos, Air Master & System Air
NOTES:
The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
Muslin cloth cover for all air outlets during construction.
Pressure testing of complete duct work as per DW/ SMACNA standard.
Silicon sealant for longitudinal & transverse joints as per specification.
Diffusers & grilles shall be powder coated as per color approved by Architect.
5 | THERMAL & ACOUSTIC INSULATION:
5.1 | THERMAL INSULATION
| Supply & fixing of Thermal insulation for supply air duct using 13mm thick class " O " Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended low VOC adhesive. | Sq.mtr | 250
Make: Armaflex & K-flex
Note:
a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
c. | Thermal insulation shall be internal for Elliptical / Expossed ducting.