## SUMMARY
AJ KITCHEN @ AHMEDABAD
SUMMARY FOR ELECTRICAL WORKS
DATE : 9.12.2023
Sr. No. | DESCRIPTION |  | TOTAL AMOUNT IN Rs.
I | PANEL & SWITCHGEAR | Rs. | 0
II | UPS | Rs. | 0
III | DISTRIBUTION BOARDS | Rs. | 0
IV | CABLES & ACCESSORIES | Rs. | 0
V | WIRING & ACCESSORIES | Rs. | 0
VI | LIGHTING FITTINGS INSTALLATION | Rs. | 0
VII | EARTHING | Rs. | 0
VIII | MISCELLANEOUS | Rs. | 0
IX | LOW VOLTAGE SYSTEM (WIRING)
A | DATA AND TELEPHONE SYSTEM | Rs. | 0
| SUB TOTAL AMOUNT IN RS. | Rs. | 0
TAXES EXTRA AS APPLICABLE

## ELE BOQ
AJ KITCHEN @ AHMEDABAD
ELECTRICAL BOQ
DATE : 9.12.2023
SR. No | DESCRIPTION | TOTAL QTY. | UNIT | UNIT RATE | TOTAL AMOUNT
I | PANEL & SWITCHGEAR
1 | Supply, installation, testing & commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process and duly powder coated using Siemens Grey Shade No. RAL 7032. The frame structure, doors and gland plates shall have 2.0 mm thick sheets and partitions shall be with 1.6 mm thick CRCA sheet. Base channel size 75 x 40 x 6 mm of ISMC shall be provided. The panel shall be dust and vermin proof with neoprene gasket. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus bar shall be of tinned Copper with epoxy supports and shall be insulated with colour coded heat shrink sleeves. The control wiring min. 2,5 Sq.mm shall be ZHLS type. The Panel shall be provided with CTs, phase indication lamps, meters, relays and all switchgear, etc. as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant. All componants for Switchgears shall be L&T/Legrand
a | Providing & installing MAIN LT PANEL as per SLD & Spec.: | 1 | Set |  | 0
125 Amps 4 pole, 25kA MCCB as a Incomer with overload, short circuit & Earth Fault protection, Energy manager with RS485 port for BMS connectivity & 4A with SP MCB with 100/5A-3 Nos., 15VA, CL-1 CT's for metering & of AE make and phase indicating lamps Vaishno make with SPMCB
Busbar chamber - 1 set, 4 pole 125A Tinned AL. Busbar with necessary
OUTGOINGS:
i. | 32A 4P MCB – 1 Nos.
ii. | 40A 4P MCB – 2 Nos.
iii. | 63A 4P MCB – 3 Nos.
iv. | 80A 4P MCCB 16kA TM Based O/C, S/C release.
2 | Supply, installation, testing & commissioning of Switchgears.(Standard Product)
a | Supply,Installation,Testing and Commissioning of 40 Amps,4Pole MCB with ELCB at 300mAh for HVAC Outdoor Isolation all complete with mounting accessories | RO | Nos.
b | Supply,Installation,Testing and Commissioning of 32 Amps,4Pole MCB for HVAC Outdoor Isolation all complete with mounting accessories. | 1 | Nos. |  | 0
c | Supply,Installation,Testing and Commissioning of 40 Amps, DP, MCB for UPS/INVERTER Isolation all complete with mounting accessories for UPS. | 2 | Nos. |  | 0
d | Supply & installation of DOL starter L&T/Siemens/Legrand for 3 kW load | RO | Nos.
e | Supply & installation of DOL starter L&T/Siemens/Legrand for 4 kW load | RO | Nos.
f | Supply & installation of Star Delta starter as per Type-2 Coordination for 3 kW (4HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Exhaust air fan)(EXISTING UNIT PROVIDED BY MALL) | RO | Nos.
g | Supply & installation of Star Delta starter as per Type-2 Coordination for 9.3 kW (12.5HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Exhaust air fan) | RO | Nos.
h | Supply & installation of Star delta starter as per Type-2 Coordination for 5.5 kW (7.5HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Fresh air fan) | RO | Nos.
i | Supply & installation of DOL starter as per Type-2 Coordination for 2.2 kW (3.0HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For AHU) | RO | Nos.
j | Supply & installation of DOL starter as per Type-2 Coordination for 1.5 kW (2.0HP) pump load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Scrubber) | RO | Nos.
k | 80 amps 4P ELMCB 300mA with 63A 5 Pin Ray Roll Socket complete with all mounting accessories – for Indoor Legrand make model No. 6078 80 | RO | Nos.
l | 63 amps 4P ELMCB 300mA with 63A 5 Pin Ray Roll Socket complete with all mounting accessories – for Indoor Legrand make model No. 6078 80 | RO | Nos.
m | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make model No. 6078 80 | RO | Nos.
n | 25 amps 4P MCB with 25A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make model No. 6078 80 | RO | Nos.
o | 25A Rey roll socket complete with 25 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | RO | Nos.
p | 20A Rey roll socket complete with 32 amps DPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | 9 | Nos. |  | 0
q | 5/15A Rey roll socket complete with 15 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | 5 | Nos. |  | 0
r | Set of 1no 25A Metal clad Socket with MCB, and 2nos 6/16A Switch sockets housed in Fabricated SS Panel suitable for hanging arrangement for Kitchen equipments. | RO | Nos.
3 | SITC of Standalone Gas leak detector with inbuilt sounder for Kitchen | RO | Nos.
| TOTAL FOR MAIN PANEL & SWITCHGEAR |  |  |  | 0
II | INVERTER / UPS
1 | Supply, Installation, testing and commissioning of 6 KVA UPS System Single Phase I/C & Single Phase O/G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings & the specifications. | 1 | Nos |  | 0
| TOTAL FOR UPS |  |  |  | 0
III' | DISTRIBUTION BOARDS
Supply, installation, testing & commissioning of Distribution Boards surface / flush mounted with Double door containing MCB/ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs/RCCB should be of 30mA/100 mA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be 'D' type and other MCBs shall be 'C' category for lighting and raw power DB LEGRAND/L&T
1 | Lighting Distribution Board - LPDB | 1 | Nos. |  | 0
8 WAY TPN DB
I/C- 1 # 32A FP MCB , 10KA
SUB I/C - 3 # 25A DP RCCB 30mA per phase
O/G - 18 # 10A SP MCB
2 | RAW Power Distribution Board - RPDB | RO | Nos.
6(8) WAY TPN DB
I/C- 1 #40 A FP MCB
SUB I/C- 3#40 DP ELCB 300mA per ph
O/G - 18 # 16/20A SP MCB
3 | Kitchen Power DB - (KPDB-1) | 1 | Nos. |  | 0
12 WAY TPN DB
I/C- 1 #80 A FP MCB
SUB I/C- 3#63 DP ELCB 100mA per ph
O/G - 30 # 16/20A SP MCB
4 | EMERGENCY LIGHTING DB (ELDB) | 1 | Nos. |  | 0
12 way SPN DB
Incomer: 40A DP RCBO 30mA
Outgoings :10/16 SP MCB, 'D' Type – 8 Nos
| TOTAL FOR DISTRIBUTION BOARDS |  |  |  | 0
IV | CABLES & ACCESSORIES
Supply & installation of following LT XLPE FRLS cables (FINOLEX/RR KABLE/POLYCAB) rated for 600 / 1100 volts AC as per IS standard 1554 Part 1 with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20 mtrs and ten finally with metal identification tags showing the size and the location from/to the specific Panel/DB at both ends.
1 | 3.5C x 300 Sq. mm A2XFY | RO | Mtr.
2 | 3.5C x 240 Sq. mm A2XFY | RO | Mtr.
3 | 3.5C x 185 Sq. mm A2XFY | RO | Mtr.
4 | 3.5C x 150 Sq. mm A2XFY | RO | Mtr.
5 | 3.5C x 120 Sq. mm A2XFY | RO | Mtr.
6 | 3.5C x 95 Sq. mm A2XFY | RO | Mtr.
7 | 3.5C x 70 Sq. mm A2XFY | RO | Mtr.
8 | 3.5C x 50 Sq. mm A2XFY | RO | Mtr.
9 | 3.5C x 35 Sq. mm A2XFY | 100 | Mtr. |  | 0
10 | 4C x 16 Sq. mm A2XFY | 20 | Mtr. |  | 0
11 | 4C x 10 Sq. mm A2XFY | RO | Mtr.
12 | 4C x 10 Sq. mm 2XFY ( Cu ) | RO | Mtr.
13 | 4C x 16 Sq. mm 2XFY ( Cu ) | RO | Mtr.
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | 15 | Mtr. |  | 0
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) | 15 | Mtr. |  | 0
16 | 4C x 2.5 Sq. mm 2XFY Cable ( Cu ) | RO | Mtr.
17 | 3C x 6sq. mm YWY cable ( Cu ) | 15 | Mtr. |  | 0
18 | 3C x 4sq. mm YWY cable ( Cu ) | 40 | Mtr. |  | 0
19 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | RO | Mtr.
20 | 1C x 10 Sq. mm YY cable ( Cu ) | RO | Mtr.
21 | 1C x 6 Sq. mm YY cable ( Cu ) | RO | Mtr.
22 | 1C x 4 Sq. mm YY cable ( Cu ) | RO | Mtr.
23 | 5Rx1Cx16 Sq.mm YY FRLS Cable (Cu) | RO | Mtr.
24 | 5Rx1Cx10 Sq.mm YY FRLS Cable (Cu) | RO | Mtr.
25 | 5Rx1Cx6 Sq.mm YY FRLS Cable (Cu) | RO | Mtr.
26 | 5Rx1Cx4 Sq.mm YY FRLS Cable (Cu) | RO | Mtr.
B | Termination of following sizes of cables with Single compression cable gland.(COMET/BRAKO)
1 | 3.5C x 300 Sq. mm A2XFY | RO | Nos.
2 | 3.5C x 240 Sq. mm A2XFY | RO | Nos.
3 | 3.5C x 185 Sq. mm A2XFY | RO | Nos.
4 | 3.5C x 150 Sq. mm A2XFY | RO | Nos.
5 | 3.5C x 120 Sq. mm A2XFY | RO | Nos.
6 | 3.5C x 95 Sq. mm A2XFY | RO | Nos.
7 | 3.5C x 70 Sq. mm A2XFY | RO | Nos.
8 | 3.5C x 50 Sq. mm A2XFY | RO | Nos.
9 | 3.5C x 35 Sq. mm A2XFY | 2 | Nos.
10 | 4C x 16 Sq. mm A2XFY | 4 | Nos. |  | 0
11 | 4C x 10 Sq. mm A2XFY | RO | Nos.
12 | 4C x 10 Sq. mm 2XFY ( Cu ) | RO | Nos.
13 | 4C x 16 Sq. mm 2XFY ( Cu ) | RO | Nos.
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | 4 | Nos. |  | 0
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) | 4 | Nos. |  | 0
16 | 4C x 2.5 Sq. mm 2XFY Cable ( Cu ) | RO | Nos.
17 | 3C x 6sq. mm YWY cable ( Cu ) | 12 | Nos. |  | 0
18 | 3C x 4sq. mm YWY cable ( Cu ) | RO | Nos.
19 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | RO | Nos.
20 | 1C x 10 Sq. mm YY cable ( Cu ) | RO | Nos.
21 | 1C x 6 Sq. mm YY cable ( Cu ) | RO | Nos.
22 | 1C x 4 Sq. mm YY cable ( Cu ) | RO | Nos.
23 | 5Rx1Cx16 Sq.mm YY FRLS Cable (Cu) | RO | Nos.
24 | 5Rx1Cx10 Sq.mm YY FRLS Cable (Cu) | RO | Nos.
25 | 5Rx1Cx6 Sq.mm YY FRLS Cable (Cu) | RO | Nos.
26 | 5Rx1Cx4 Sq.mm YY FRLS Cable (Cu) | RO | Nos.
| TOTAL FOR CABLES & ACCESSORIES |  |  |  | 0
V | WIRING & ACCESSORIES
Notes :
1) Rates for point wiring shall include supply & installation of Wires & wiring acccessories such as angle holders/ceiling roses as required. conduits, conduit accessories such as junction boxes, Ts, elbows etc,Switches, sockets & fixtures shall not be included in the point wiring rates. These will be counted & paid separately.
2) Unless otherwise specified, all wires in point wiring shall be 2.5 sq.mm
Stranded copper conductor 1.1 KV grade, I.S.I. marked (P+N+E),
LSZH) PVC insulated .
Wires shall be colour coded (Red, Yellow and Blue for Phases,
Black for Neutral & Green for earth).
3) Looping of wires shall be in fittings and switch boxes only
4) Location of switches/sockets/ DBs shown on the drawings shall
be confirmed with the Architect/ Consultant/ Project Manager
before installation.
5) All Surface and concealed Conduits shall be rigid GI conduits of
size not less than 20 mm dia as per applicable IS.
6)The Contractor can take more than one circuit in the same conduit
provided they are of the same phase. The size of conduit shall be
decided according to the number of wires in it as per applicable IS & as
specified.
7) Payments for light fixtures & fans will be made separately as per the
items given in 'Light Fixtures & Accessories'.
8) Type & location of light fixtures shown in the drawings are
tentative and subject to revision as per the recommendation of
Architect/ Consultant. The quantities (number of points and accessories)
of point wiring will be revised as actual installed on account of such
revisions in the layouts.
9) Circuit wiring from DBs to the switch boards or first light point shall
Be included as primary points & remaining points of the same looping
shall be considered as Secondary points and shall be counted in nos.
10) Circuit Wiring from DB to Kitchen Power points shall be measured in running meters
1 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included.
Averagepoint length of primary&secondaryto be derived by Contractor, fromthe drawing provided AND+/-1MtrMeasured Radially
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | 8 | Nos. |  | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | 25 | Nos. |  | 0
2 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Switch Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same switch board where primary points are controlling. The Power points shall be measured in Nos. Cost of FRLS PVC conduits, 6A switch & switch board and accessories shall be included.
a) | Primary Light points controlled by Switch (3R x 2.5 sqmm wire) | 2 | Nos. |  | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) |  | Nos. |  | 0
c) | DB to SB & SB to SB circuit wiring : For Switch Operated Primary point @ SB to SB loop point. Wiring for switch board controlled by MCB already installed in DB by using 3 X 2.5 sq. mm flexible LSZH copper wires in 25mm GI conduits as per IS 9537 part-3 or surface mounted. | 10 | Mtrs |  | 0
3 | Supply, installation, testing & commissioning of point wiring for Emargency light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of FRLS PVC conduits and accessories shall be included.
Averagepoint length of primary&secondaryto be derived by Contractor, fromthe drawing provided AND+/-1MtrMeasured Radially
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | 1 | Nos. |  | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) |  | Nos. |  | 0
5 | Providing point wiring for Raw Power points 1no. 6/16A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 4.0 sq. mm copper conductor wires and minimum 4.0 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect / Consultant. (Cost of FRLS PVC Conduit / Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be LSZH type ) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | 2 | Nos. |  | 0
b) | Secondary points | 2 | Nos. |  | 0
6 | Providing point wiring for Raw Power points 1no. 6A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 2.5 sq. mm copper conductor wires and minimum 2.5 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect / Consultant. (Cost of Conduit / Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be FRLS type ) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | 4 | Nos. |  | 0
b) | Secondary points | 6 | Nos. |  | 0
8 | Supply and laying of following PVC insulated copper conductor 1100 volt grade stranded flexible LSZH wire in already laid GI conduit concealed or surface mounted making connections where ever required to complete the installation.(For Kitchen and Bar Power Points) Conduit rate shall be paid separately.
a) | 2R x 2.5Sqmm + 1R x 2.5Sqmm Cu. Wires | 120 | Mtr. |  | 0
b) | 3R x 4Sqmm Cu. Wires | 228 | Mtr. |  | 0
c) | 4R x 4Sqmm + 2R x 2.5Sqmm Cu. Wires |  | Mtr. |  | 0
d) | 4R x 6Sqmm + 2R x 2.5Sqmm Cu. Wires |  | Mtr. |  | 0
9 | Supply & installation of 25 mm dia. GI conduit with pull box / junction box & all accessories for Kitchen & Bar Power wiring as per the requirement
a | - do - but conduit pipe shall be Rigid type. | 225 | Mtr. |  | 0
b | - do - but flexible conduit pipe | 25 | Mtr. |  | 0
10 | Supply & installation of 20 mm dia. GI conduit with pull box / junction box & all accessories for Lighting & Power wiring as per the requirement
a | - do - but conduit pipe shall be Rigid type. | RO | Mtr.
b | - do - but flexible conduit pipe | RO | Mtr.
11 | Supply and installation of Perforated Cable Tray (ASIAN)out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant/Architect
a | 300 x 50 x 2mm | RO | Mtr.
b | 200 x 50 x 2mm | RO | Mtr.
c | 150 x 50 x 2mm | 25 | Mtr. |  | 0
d | 100 x 50 x 2mm | RO | Mtr.
e | 50 x 50 x 2mm | RO | Mtr.
12 | Supply and installation of GI trunking (SV POWER/ASIAN) with 2 mm thickness & properties/clamps for suspension at appropriate intervals & as per the route approved by Architect/Consultant. (For DATA/CONTROL WIRING/LIGHTING & POWER CIRCUITS / KITCHEN)
a | 300 x 50 x 2mm | RO | Mtr.
b | 200 x 50 x 2mm | RO | Mtr.
c | 150 x 50 x 2mm | RO | Mtr.
d | 100 x 50 x 2mm | RO | Mtr.
e | 50 x 50 x 2mm | 20 | Mtr. |  | 0
13 | Supply and installation of GI raceway with 2 mm thickness & proper ties/clamps at appropriate intervals & as per the route approved by Architect/Consultant. (Cost of cutting the floor for laying of raceways to be included).
a | 3 runs of underfloor raceways of size 100 x 40 mm | RO | Mtr.
b | 2 runs of underfloor raceways of size 100 x 40 mm | RO | Mtr.
c | 1 runs of underfloor raceways of size 100 x 40 mm | RO | Mtr.
d | 1 runs of underfloor raceway of size 85 x 40 mm | RO | Mtr.
e | 2 runs of underfloor raceway of size 65 x 40 mm | RO | Mtr.
f | 1 runs of underfloor raceway of size 65 x 40 mm | RO | Mtr.
14 | Supply & installation of GI junction boxes with 2 mm thickness, 2mm thick SS cover with 2” extra on all sides SS cover on top and having screw fixed plates on all four sides with knock out holes for conduits. The plates shall be retained on the sidezs having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be prepared as per the final approval of Architect/Consultant. The junction boxes shall be protected from the entry of unwanted material till the completion of the project & the SS plates shall be installed after the final polishing of flooring.
a | suitable for 450 x 450 x 50 mm | RO | Nos.
b | suitable for 350 x 350 x 50 mm | RO | Nos.
c | suitable for 250 x 250 x 50 mm | RO | Nos.
d | suitable for 150 x 150 x 50 mm | 2 | Nos. |  | 0
15 | Supply, installation, testing & commissioning of flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect/Consultant
a | 6A one way plate type switch | 4 | Nos. |  | 0
b | 6A 5 pin Socket outlet | RO | Nos.
c | 6A 5pin switch socket outlet for CCTV & Charging point | 12 | Nos. |  | 0
f | 3 nos. 6A socket controlled by 3no 6A switch | RO | Nos.
g | 2 nos. 6A socket controlled by 2no 16A switch |  | Nos.
h | 1 nos. 6/16A socket controlled by1nos 6/16A switch | 30 | Nos. |  | 0
l | I phase, 2 Nos x 5/15 amp, bakelite socket & switch, housed in Fabricated SS Panel suitable for hanging arrangement for Kitchen equipments. (having Two outlet /6 modular plate) | 1 | Nos. |  | 0
16 | Supplying, installation, Testing and commissioning flush mounting floor metallic boxes IP 66 (at terrace level) with 2 nos of 6/16A International switch & socket outlet + 1 set of blanking plate for 2 data/voice outlet suitable for AMP tyco I/o's of following modules complete with all installation kits, accessories, required to finish the installation – Sample will Approved by Client/Consultant. Cost of Switches, sockets outlet & blanking plat for Data/Voice outlets shall be included.
16.1 | 300mm x 300mm x 65/75 mm | RO | Nos.
17 | Supply, installation of temporary lighting & power arrangement for construction purpose of with industrial type switch & sockets/MCB's/ELCB's & lighting fittings as required to finish the work for interior contractor & necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules & regulations as per Airport Security Department. The material shall be taken back by the contractor. | 1 | Job |  | 0
| TOTAL FOR WIRING & ACCESSORIES |  |  |  | 0
VI | LIGHTING FITTINGS
Installation, testing & commissioning of the following concealed / surface mounted or suspended light fixtures AS PER FINAL APPROVAL FROM ARCHITECT/CLIENT/CONSULTANT with lamps, ballast & all necessary mounting & supporting accessories. No additional cost shall be paid for supporting.
0
1 | 600x600mm PANEL LIGHT | 1 | Nos. |  | 0
2 | SURFACE LIGHT | 1 | Nos. |  | 0
3 | PENDANT LIGHT-1 | 4 | Nos. |  | 0
4 | PENDANT LIGHT-2 | 11 | Nos. |  | 0
5 | COB LIGHT | 5 | Nos. |  | 0
6 | DECORATIVE WALL LIGHT | 5 | Nos. |  | 0
7 | LED STRIP LIGHT | 40 | Mtr. |  | 0
8 | HOOD LIGHT | 5 | Nos. |  | 0
9 | 600x600mm PANEL LIGHT (Emg) | 1 | Nos. |  | 0
10 | PENDANT LIGHT-1 (Emg) | 2 | Nos. |  | 0
| TOTAL FOR LIGHTING FIXTURES |  |  |  | 0
VII | EARTHING
1 | Supply and Installation of Maintenance Free Chemical earthing using Electrode of Size approx. 38 mm dia +/- 2mm, 3 metres long bonded with 50x6 copper internal strip complete with excavation, civil works, cast iron cover with backfill compound min. 40 KG. The system shall be CPRI tested. Warranty period of chemical earthing from the date of commissioning shall be 5 years. Warranty implies the voltage between earth and neutral will not exceed 0 volts for earthing pits installed. (Note: Body earthing provided by Base builder. We have considered Neutral earthing for UPS & Server racks.) | RO | Nos.
2 | Supply & erection of G.I. strip of 50 x 6 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | RO | Mtr.
3 | Supply & erection of G.I. strip of 25 x 3 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | 60 | Mtr. |  | 0
4 | 1 no. 4 sq. mm YY cable in 25mm GI conduit for earthing FOR NETWORK RACK | 45 | Mtr. |  | 0
5 | Supplying & erecting bare copper conductor of 8 swg for earthing purpose | 80 | Mtr.
7 | Supplying & erecting bare GI conductor of 8 swg for earthing purpose |  | Mtr. |  | 0
8 | Supplying & erecting bare CU conductor of 12 swg for earthing purpose |  | Mtr.
9 | Supplying & installation testing & commissioning of earth terminal box |  | Nos. |  | 0
| TOTAL FOR EARTHING |  |  |  | 0
VIII | MISCELLANEOUS
1 | Supply & Installation of 6A 3 pin plug top | 5 | Nos.
2 | Supply & Installation of 16A 3 pin plug top | 6 | Nos.
3 | Supply, installation, testing & commissioning of Cat-6 FRLS Cable for Lighting Automation | RO | Mtr.
4 | Supply & laying of Rubber Mats, CPRI tested conforming to standards like BS 921, ASTM-D 178 & IEC 479 for different operatng voltage ratings as below.
| Supply of 2M x 1M Rubber mat suitable for operatng voltage upto 1.1 KV | 1 | Set |  | 0
5 | Supply & fixing of approved shock treatment chart written in English and in local Language. The chart shall be framed in Teakwood and covered with glass. | 1 | Nos. |  | 0
6 | Supply & fixing of approved Fire Alarm evacuation plan chart written in English and in local Language approved by cleint requrements. | RO | Nos
7 | Supply & fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language | 1 | Nos. |  | 0
8 | Supply & handed over to client of First Aid Box | RO | Set
9 | SITC of Emergency Exit signage (battery operated) approval by client / architect / consultant. Make: Prolite or Equivalent | RO | Nos.
| TOTAL FOR MISELANIOUS |  |  |  | 0
IX | LOW VOLTAGE SYSTEM
A | DATA AND TELEPHONE SYSTEM
1 | Supply & Installation of 25mm.dia. GI conduit with pull box/ junction box & all accessories for DATA /VOICE/WIFI wiring as per the requirement. | 120 | Mtr. |  | 0
2 | Providing DATA wiring inside 25mm dia GI conduit from each Data outlet to ICT CP Point by using Indoor Type CAT6A, | 200 | Mtr. |  | 0
3 | Supply & Installation of Internet Jack Unit RJ-45 suitable for CAT6A | 8 | Nos. |  | 0
4 | Supply & Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 3 Feet | 8 | Nos. |  | 0
5 | Supply & Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 7 Feet | 8 | Nos. |  | 0
6 | Supply & laying indoors multi-pair 0.5mm dia copper PVC insulated and sheathed, armoured telephone cables on walls, ceiling, cable trays, trunking complete with clamps, cable markers etc. from MDF to the various tag blocks as specified
a | 10 pair cable armoured | 40 | Mtr. |  | 0
b | 5 pair cable | RO | Mtr.
c | 3 pair cable | RO | Mtr.
d. | 2 pair cable | RO | Mtr.
7 | Supply & installation of telephone tag block with KRONE terminal connectors, G.I.J.B as specified & com-plete with all interconnections and jumper connections bet-ween the two tag blocks on all floors as shown on drgs.
a | 50 pair tel. tag block | RO | Nos.
b | 20 pair tel. tag block | 1 | Nos. |  | 0
c | 10 pair tel. tag block | RO | Nos.
| TOTAL FOR DATA AND TELEPHONE SYSTEM |  |  |  | 0