## SUMMARY
AJ CAFÉ - AHMEDABAD AIRPORT
SUMMARY FOR ELECTRICAL LOAD
REVISION: R0, DATE: 09.12.2023
Sr.No. | DESCRIPTION | WATTAGE (KW) | No of Units | CONNECTED LOAD | MAX. DMD LOAD | DIVERSITY | UPS LOAD
1 | LIGHTING LOAD
a | 600x600mm PANEL LIGHT | 30 | 1 | 0.03 | 0.027 | 90%
b | SURFACE LIGHT | 22 | 1 | 0.022 | 0.0198 | 90%
c | PENDANT LIGHT-1 | 18 | 4 | 0.072 | 0.0648 | 90%
d | PENDANT LIGHT-2 | 18 | 11 | 0.198 | 0.1782 | 90%
e | COB LIGHT | 12 | 5 | 0.06 | 0.054 | 90%
f | WALL LIGHT | 12 | 4 | 0.048 | 0.0432 | 90%
g | LED STRIP LIGHT | 22 | 40 | 0.88 | 0.792 | 90%
h | HOOD LIGHT | 10 | 2 | 0.02 | 0.018 | 90%
i | 600x600mm PANEL LIGHT (Emg) | 30 | 1 | 0.03 | 0.027 | 90% | 0.03
j | PENDANT LIGHT-1 (Emg) | 18 | 2 | 0.036 | 0.0324 | 90% | 0.036
2 | RAW POWER LOAD
| 6/16A Utlity sockets | 0.1 | 9 | 0.9 | 0.36 | 40%
| USB | 0.01 | 5 | 0.05 | 0.02 | 40%
| POS counters | 0.3 | 2 | 0.6 | 0.48 | 80% | 0.6
| KOT | 0.2 | 0 | 0 | 0 | 100% | 0
| Chilling Machine | 1 | 0 | 0 | 0 | 100% | 0
| Self Service Kiosk | 0.25 | 0 | 0 | 0 | 100%
| Signage | 1 | 3 | 3 | 3 | 100% | 3
| R.O. Plant | 0.15 | 0 | 0 | 0 | 100%
| Service Station | 0.3 | 0 | 0 | 0 | 100%
| TV | 0.25 | 1 | 0.25 | 0.25 | 100% | 0.25
| GAS SUPPRESSION SYETEM | 0.15 | 1 | 0.15 | 0.15 | 100% | 0.15
| FIRE SUPPRESSION SYSTEM | 0.15 | 1 | 0.15 | 0.15 | 100% | 0.15
3 | HVAC LOAD
| AHU | 1.1 | 1 | 1.1 | 0.88 | 80%
0
4 | KITCHEN EQUIPMENTS |  |  | 33.345 | 23.3415 | 70%
5 | FRESH AIR | 2.2 | 0 | 0 | 0 | 80%
6 | EXHAUST BLOWER | 1.5 | 0 | 0 | 0 | 80%
.
7 | MISCELLANEOUS |  |  | 1 | 0.5 | 50%
| TOTAL LOAD IN KW |  |  | 41.941 | 30.3879 |  | 4.216
UPS CALCULATIONS
| Total C & S Load | [5 empty] | 4216
| TOTAL EMERGENCY LOAD 15% of total lighting load | [5 empty] | 0.135
| TOTAL UPS LOAD | [5 empty] | 4216.135
| Load Factor 80% - UPS Load shall be (WATTAGE) | [5 empty] | 3372.908
| After considering 0.85 power factor - VA Rating | [5 empty] | 3968.1271
| Efficiency 80% - UPS Rating shall be (VA) | [5 empty] | 4960.1588
| Recommended UPS rating (KVA) -1PH. I/C & O/G .(with Plus Minus 5%) | [5 empty] | 4.9602
| Nearest size available--(1#3KVA) | [5 empty] | 6
.

## BOQ
SR.NO. | DESCRIPTION | OVERALL SIZE | QTY | Make | Model | ELECTRICAL |  |  |  | WATER |  |  | Drain |  | LPG / PNG |  |  | EXHAUST CFM | Tape Model Number | Tape Photo | REMARK
|  | All Dimensions in MM L x W x H |  |  |  | HP | Watts | ELECTRICAL LOAD IN KW | PHASE | HOT | COLD | RO | Size | Type of Burner | NO OF BURNER | Consumption Per Burner Per Hour | BTU Per Burner Per Hour |  |  |  |  | R PHASE | Y PHASE | B PHASE
BOH
BO - 01 | Twin Basket Deep Fat Fryer ( Table Model ) | 270 x 420 x 360 | 2 | SIRMAN | ELDORADO 8 |  | 3 .3 x 2 | 6.8 | I | [12 empty] | 3.3 |  | 3.3
BO - 02 | 6 Drawers Low Boy Chiller | 1800 x 800 x 700 | 1 | CUSTOM FABRICATED |  |  |  | 1.5 | I | [14 empty] | 1.5
BO - 03 | Gas Fired Hot Plate with 1 U/S | 500 x 700 x 350 + 150 | 1 | CUSTOM FABRICATED
BO - 04 | Work Table With 2 U/S | 575 x 800 x 700 | 1 | CUSTOM FABRICATED
BO - 05 | Four Burner Range With 1 U/S | 765 x 765 x 350 + 150 | 1 | CUSTOM FABRICATED
BO - 06 | Side Table | 450 x 765 x 350 + 150 | 1 | CUSTOM FABRICATED
BO - 07 | Reach In Freezer | 700 x 880 x 2043 | 1 | Blue Star | RF2D700GP |  | 0.522 | 0.522 | I | [12 empty] | 0.522
BO - 08 | Under Counter Dish Washing Machine | 610 x 600 x 820 | 1 | Electrolux | 400153 |  |  | 6.7 | I |  | 12 | [11 empty] | 6.7
BO - 09 | Table With Sink | 1450 x 700 x 850 + 150 | 1 | CUSTOM FABRICATED | [5 empty] | 12 | 12 |  | 100
BO - 10 | Sunken Table - For Soiled Dish | 650 x 350 x 850 + 150 | 1 | CUSTOM FABRICATED
BO - 11 | Garbage Bin | Standard | 1 | Bought Out
BO - 12 | Salad Bar With Work Top Refer | 1350 x 700 x 1056 | 1 | HOSIZAKI | RTSW137MS4-GNTE |  |  | 1 | I
BO - 13 | Spare Number
BO - 14 | Wall Shelf | 1740 x 300 | 2 | CUSTOM FABRIACTED
BO - 15 | Micro wave Oven ( 25.5 Litres Capacity ) | 511 x 432 x 311 | 1 | Celfrost | CMO 25 |  | 1000 | 1 | I | [14 empty] | 1
BO - 16 | Salad Bar With Working Table | 450 x 880 x 850 + 150 | 1 | CUSTOM FABRICATED
BO - 17 | Insect Killer | BRANDED | 2 | TECHNOCRAT |  | 1/2 HP | 0.75 | 0.75 | I | [12 empty] | 0.75
BO - 18 | Hand Sink | HACCP Standard | 1 | Custom Fabricated | [5 empty] | 12 | 12 |  | 100
BO - 19 | SS Stoarge Rack 5 Shelves - 3 Sides Up and Front Side Down | 750 x 450 x 1950 | 1 | CUSTOM FABRICATED
BO - 20 | SS Stoarge Rack 5 Shelves - 3 Sides Up and Front Side Down | 460 x 750 x 1950 | 1 | CUSTOM FABRICATED
BO - 21 | Fire Extinguisher
BO - 22 | Spare Number
BO - 23 | Exhaust Hood (Double Skin Exhaust) | 2400 x 1000 x 500 | 1 | CUSTOM FABRICATED | [13 empty] | 3157
BO - 24 | Wall Shelf | 1150 x 300 | 2 | CUSTOM FABRICATED
FOH
FO -01A | Ambient Display Cabinet
FO -01B | Pastry Cabinet | 1500 x 665 x 1235 | 1 | WESTERN | PTW15 |  |  | 1 | I | [12 empty] | 1
FO -02 | POS |  | 2
FO -03 | 3 Door Back Bar Cooler | 1345 x 545 x 900 | 1 | Western | RBW-135 | 1/2 HP | 0.373 | 0.373 | I | [13 empty] | 0.373
FO -04 | Coffee Machine Compact 2 Group Semi Automatic | 784 x 545 x 498 | 1 | Nuvo Simonelli | APPIA LIFE - 2 |  | 4.6 | 4.6 | I |  |  | 12 | 38 | [10 empty] | 4.6
FO -05 | Knock Box | Standard | 1 | Bought Out
FO -06 | Cup Rinser | Standard | 1 | [7 empty] | 12 |  | 100
FO -07 | Coffee Grinder | 210 x 480 x 470 | 1 | Otto | Regular |  | 0.35 | 0.35 | I | [12 empty] | 0.35
FO -08 | Garbage Bin | Standard | 1 | Bought Out
FO -09 | Counter Model Sink - SS | 400 x 400 x 210 | 1 | CUSTOM FABRICATED |  |  |  |  | 1 | 12 | 12 |  | 100
FO -10 | Under Counter Ice Cube Machine | 550 x 550 x 800 | 1 | Manitowoc | UG - 50 | [6 empty] | 12 |  | 100
FO -11 | Blender | 213 x 200 x 416 | 2 | JTC | TM -800 |  | 0.6 | 0.6 | I | [14 empty] | 0.6
FO -12 | High Speed Oven | 356 x 648 x 629 | 1 | MerryChef | Connex 12 Standard Power |  | 3680 | 3.6 | I | [13 empty] | 3.6
FO -13 | Three Door Under Counter Refrigerator ( Compressor on LHS) | 1805 x 700 x 850 | 1 | Blue Star | UC3100GP | 0.75 | 0.75 | 0.55 | I | [12 empty] | 1.5
FO -14 | Insect Killer | BRANDED | 1 | TECHNOCRAT |  | 1/2 HP | 0.75 | 0.75 | I
FO -15 | Fire Extinguisher
EXT - 01 | Grease Trap |  | 2
| GEYSER |  | 1 |  |  |  | 3 | [14 empty] | 3
| REFRIGERATOR |  | 1 |  |  |  | 0.5 | [15 empty] | 0.5
| DISPLAY COUNTER |  | 1 |  |  |  | 0.5 | [16 empty] | 0.5
| ICE CUBE MACHINE |  | 1 |  |  |  | 0.2 | [16 empty] | 0.25
| TOTAL | [20 empty] | 10.422 | 11.173 | 11.75
33.345