## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
13.3 | FIRE ALARM SYSTEM (MAKE: SIMPLEX) Detectors and Devices
13.3.1 | Supply,Installation,Testing & Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices & shall be capable of providing DPDTcontact rated at 24V DC, 2A.Make - Simplex - 4090-9001 | Nos | 1
13.3.2 | Supply,Installation,Testing & Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system for AHU tripping and shall be capable of providing DPDTcontact rated at 24v DC, 2A. (For all AHU's, Fans & Acess Control) | Nos | 2
13.3.3 | Supply,Installation,Testing & Commissioning of Horn / Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with Control modules and necessary accessories including back box. Make - Simplex - 49CMTV-WRF | Nos | 3
13.3.4 | Supply, Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors( Below False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. Make - Simplex - 4098-9714 | Nos | 9
13.3.7 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Heat Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. Make - Simplex - 4098-9733 | Nos | 1
13.3.8 | Supply,Installation,Testing & Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressable module that monitors and reports contact status. Make - Simplex - 4099-9006 | Nos | 3
13.4 | SITC of Fault Isolator. Make - Simplex - 4090-9116 | Nos | 1
13.5 | SITC of 2Cx1.5sq.mm multistranded FRLSH Cu. Armoured for RED Colour,Mylan Shielded Screened cable. (Make-Polycab) For SLC | Mtrs | 180
13.6 | SITC of 2Cx2.5sq.mm multistranded FRLSH Cu. Armoured for RED Colour,Mylan Shielded Screened cable. (Make-Polycab) For NAC. | Mtrs | 30