## SUMMARY
SUBWAY @ DIAL
SUMMARY FOR ELECTRICAL LOAD
REVISION: R0, DATE: 30.11.2023
UPS LOAD
Sr.No. | DESCRIPTION | WATTAGE (KW) | No of Units | CONNECTED LOAD | MAX. DMD LOAD | DIVERSITY
1 | LIGHTING LOAD
a | RECESSED LED DOWN LIGHT | 40 | 12 | 0.48 | 0.432 | 90%
g | RECESSED LED DOWN LIGHT ( E) | 40 | 5 | 0.2 | 0.18 | 90% | 0.2
2 | RAW POWER LOAD
| 6/16A Utlity sockets | 0.1 | 4 | 0.4 | 0.16 | 40%
| POS counters | 0.3 | 1 | 0.3 | 0.24 | 80% | 0.3
| MANAGER PC | 0.25 | 1 | 0.25 | 0.25 | 100% | 0.25
| Menu Board | 0.25 | 6 | 1.5 | 1.5 | 100% | 1.5
| Self Service Kiosk | 0.25 | 0 | 0 | 0 | 100%
| Signage | 1 | 1 | 1 | 1 | 100%
3 | HVAC LOAD
| AHU | 1.5 | 1 | 1.5 | 1.2 | 80%
| FRESH AIR FAN | 1.1 | 1 | 1.1 | 0.88 | 80%
| EXHAUST FAN | 1.1 | 1 | 1.1 | 0.88 | 80%
0
4 | KITCHEN EQUIPMENTS |  |  | 15.49 | 10.843 | 70%
5 | MISCELLANEOUS |  |  | 1 | 0.5 | 50%
| TOTAL LOAD IN KW |  |  | 24.32 | 18.065 |  | 2.25
UPS CALCULATIONS
| Total C & S Load | [5 empty] | 2250
| Load Factor 80% - UPS Load shall be (WATTAGE) | [5 empty] | 1800
| After considering 0.85 power factor - VA Rating | [5 empty] | 2117.6471
| Efficiency 80% - UPS Rating shall be (VA) | [5 empty] | 2647.0588
| Recommended UPS rating (KVA) -1PH. I/C & O/G .(with Plus Minus 5%) | [5 empty] | 2.6471
| Nearest size available--(1#3KVA) | [5 empty] | 3

## KITCHEN LOAD
Electrical Load Distribution and SLD Details DELHI AIRPORT
S No. | Description | QTY | Load | Unit Load |  |  | MCCB /MCB | Supply Type | Demand Load | Diversity Factor | Maximum Demand
|  |  |  | R | Y | B
| Baking Oven (NUVU/Etc) | 1 | 7.2 | 7.2 |  |  | 32A,4P,MCB | 3PH | 7.2 | 0.3 | 2.16
| Speed Oven (Merry Chef, Turbo Chef) | 1 | 6.5 | 6.5 |  |  | 32A,4P,MCB | 3PH | 6.5 | 0.7 | 4.55
1 | Microwave | 1 | 1 | 1 |  |  | 16A,SP,MCB | 1PH | 1 | 0.5 | 0.5
2 | Spare power socket | 1 | 0.5 |  | 0.5 |  | 16A,SP,MCB | 1PH | 0.5 | 0.4 | 0.2
3 | 4 door chiller | 1 | 0.8 | 0.8 |  |  | 16A,SP,MCB | 1PH | 0.8 | 0.7 | 0.56
4 | 2 door freezer | 1 | 1 | 1 |  |  | 25A,SP,MCB | 1PH | 1 | 0.7 | 0.7
5 | SPARE | 0 | 0.4 |  | 0 |  | 16A,SP,MCB | 1PH | 0 | 0.4 | 0
6 | Visi Cooler | 1 | 0.8 |  | 0.8 |  | 16A,SP,MCB | 1PH | 0.8 | 0.6 | 0.48
7 | SPARE | 0 | 1 |  | 0 |  | 16A,SP,MCB | 1PH | 0 | 0.6 | 0
8 | Spare power socket | 1 | 0.5 |  | 0.5 |  | 16A,SP,MCB | 1PH | 0.5 | 0.4 | 0.2
9 | Air curtain | 1 | 1 |  | 1 |  | 16A,SP,MCB | 1PH | 1 | 0.6 | 0.6
10 | Griller | 1 | 1.6 |  | 1.6 |  | 6A,SP,MCB | 1PH | 1.6 | 0.7 | 1.12
11 | Sandwich station Veg | 1 | 1 |  |  | 1 | 16A,SP,MCB | 1PH | 1 | 0.8 | 0.8
12 | 4 door freezer | 1 | 1 |  |  | 1 | 16A,SP,MCB | 1PH | 1 | 0.6 | 0.6
13 | PMX fountain machine * Ice Machine | 0 | 1.5 |  |  | 0 | 16A,SP,MCB | 1PH | 0 | 0.7 | 0
14 | Sandwich station Non veg | 1 | 1 |  |  | 1 | 10A,SP,MCB | 1PH | 1 | 0.8 | 0.8
15 | Geyser | 1 | 1 |  |  | 1 | 25A,SP,MCB | 1PH | 1 | 0.5 | 0.5
16 | RO Point | 1 | 1 | 1 |  |  | 16A,SP,MCB | 1PH | 1 | 0.8 | 0.8
17 | INSECT KILLER | 2 | 0.15 |  |  | 0.3 | 6A,SP,MCB | 1PH | 0.15 | 0.8 | 0.12
18 | R.O PRESSURE PUMP+ SPARE | 1 | 1 | 1 |  |  |  | 1PH | 1 | 0.8 | 0.8
0
0
| TOTAL |  |  | 4.8 | 4.4 | 4.3 | 63A, 4P MCB | TOTAL LOAD | 30.66 | DIVERSIFIE D LOAD | 8.78
Total Electric Load | [6 empty] | 1~220 V |  |  |  | 8.78
[7 empty] | 3~N 415 V |  |  |  | 6.71
[7 empty] | Total Conected load |  |  |  | 15.49 | kw