## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price
I | PANEL & SWITCHGEAR
1 | Supply, installation, testing & commissioning of Switchgears.(Standard Product)
| MAIN PANEL-1 | Nos. | 1
Incomer : 63 AMPS 4P MCB, 10kA
Meter & Protection: ELR with CBCT; 60/5A, 15VA, CL-1 CT's -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
Indication: Phase indicating lamps with 6A MCB
Busbar: 75A TPN AL Busbar
Outgoings:
a) 63A 4P MCB, C TYPE - 3 Nos
b) 40A 4P MCB, C TYPE - 2 Nos
c) 32A DP MCB, C TYPE - 2 Nos
d) 20A 4P MCB, C TYPE - 2 Nos
e) MPCB SUITABLE for 1.5 kw motor DOL Starter, Phase Indicating lamps, ON/OFF/TRIP Indication, ON/OFF Push Button-1 Nos.
f) MPCB SUITABLE for 1.1 kw motor DOL Starter, Phase Indicating lamps, ON/OFF/TRIP Indication, ON/OFF Push Button-2 Nos.
1.1 | Supply,Installation,Testing and Commissioning of 20 Amps,DP ELMCB 100mA for HVAC Outdoor Isolation all complete with mounting accessories | Nos.
1.2 | Supply,Installation,Testing and Commissioning of 63 Amps,3Pole MCB for HVAC Outdoor Isolation all complete with mounting accessories. | Nos.
1.3 | Supply,Installation,Testing and Commissioning of 40 Amps,4Pole MCB for HVAC Outdoor Isolation all complete with mounting accessories. | Nos. | 3
1.4 | Supply,Installation,Testing and Commissioning of 32 Amps, DP, MCB for UPS Isolation all complete with mounting accessories for UPS. | Nos. | 2
1.14 | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make model No. 6078 80 | Nos. | 2
1.17 | 20/32A Rey roll socket complete with 25 amps SPMCB with 3 pin metal clad socket & Plug top | Nos. | 2
I) 25A, 3Pin industrial metal clad Socket with MCB – 1nos
I) 20A, 3Pin industrial metal clad Socket with MCB – 1nos
ii)set of 2nos 16A Bakelite Socket with 2nos 16A Switch –3nos
iii) Data Socket – 2nos
iv) Telephone Socket – 1no.
II | UPS
1 | Supply, Installation, testing and commissioning of 3.0 KVA UPS System Single Phase I/C & Single Phase O/G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings & the specifications. | Nos. | 1
III' | DISTRIBUTION BOARDS
Supply, installation, testing & commissioning of Distribution Boards surface / flush mounted with Double door containing MCB/ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs/RCCB should be of 30mA/100/300 mA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be 'D' type and other MCBs shall be 'C' category for lighting and raw power DB.
2 | Kitchen Power DB - KPDB | Nos. | 1
8 way TPN DB
I/C-63A FP MCB -1 Nos
SUB I/C: 40A DP RCCB @ 100mA - 3 Nos
O/G -18 # 10/16/20A SP MCB
3 | LDB | Nos. | 1
12 way SPN DB
I/C-32A RCBO 30mA-1 Nos
O/G -8 # 6/10A SP MCB
4 | UPSDB | Nos. | 1
12 way SPN DB
I/C-32A RCBO 30mA-1 Nos
O/G -8 # 6/10A SP MCB
IV | CABLES & ACCESSORIES
Supply & installation of following LT XLPE FRLS cables rated for 600 / 1100 volts AC as per IS standard 1554 Part 1 with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 10 mtrs and ten finally with metal identification tags showing the size and the location from/to the specific Panel/DB at both ends.
9 | 4C x 25 Sq. mm A2XFY | Mtr. | 30
10 | 4C x 16 Sq. mm A2XFY | Mtr. | 10
11 | 4C x 10 Sq. mm A2XFY | Mtr. | 10
12 | 4C x 10 Sq. mm 2XFY ( Cu ) | Mtr. | 10
13 | 4C x 16 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 10
14 | 4C x 6 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 10
15 | 4C x 2.5 Sq. mm 2XFY Cable ( Cu ) | Mtr. | 10
17 | 3C x 4sq. mm YWY cable ( Cu ) | Mtr. | 20
18 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | Mtr. | 80
24 | 5Rx1Cx6 Sq.mm YY FRLS Cable (Cu) | Mtr. | 45
25 | 1Rx1Cx4 Sq.mm YY FRLS Cable (Cu) | Mtr. | 50
B | Termination of following sizes of cables with Single compression cable gland.(COMET/BRAKO)
9 | 4C x 25 Sq. mm A2XFY | Nos. | 2
10 | 4C x 16 Sq. mm A2XFY | Nos. | 2
18 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | Nos. | 6
24 | 5Rx1Cx6 Sq.mm YY FRLS Cable (Cu) | Nos. | 4
25 | 1Rx1Cx4 Sq.mm YY FRLS Cable (Cu) | Nos. | 2
V | WIRING & ACCESSORIES
1) Rates for point wiring shall include supply & installation of Wires & wiring acccessories such as angle holders/ceiling roses as required. conduits, conduit accessories such as junction boxes, Ts, elbows etc,Switches, sockets & fixtures shall not be included in the point wiring rates. These will be counted & paid separately.
2) Unless otherwise specified, all wires in point wiring shall be 2.5 sq.mm
Stranded copper conductor 1.1 KV grade, I.S.I. marked (P+N+E),
(FRLSH) PVC insulated .
Wires shall be colour coded (Red, Yellow and Blue for Phases,
Black for Neutral & Green for earth).
3) Looping of wires shall be in fittings and switch boxes only
4) Location of switches/sockets/ DBs shown on the drawings shall
be confirmed with the Architect/ Consultant/ Project Manager
before installation.
5) All Surface and concealed Conduits shall be rigid GI conduits of
size not less than 20 mm dia as per applicable IS.
6)The Contractor can take more than one circuit in the same conduit
provided they are of the same phase. The size of conduit shall be
decided according to the number of wires in it as per applicable IS & as
specified.
7) Payments for light fixtures & fans will be made separately as per the
items given in 'Light Fixtures & Accessories'.
8) Type & location of light fixtures shown in the drawings are
tentative and subject to revision as per the recommendation of
Architect/ Consultant. The quantities (number of points and accessories)
of point wiring will be revised as actual installed on account of such
revisions in the layouts.
9) Circuit wiring from DBs to the switch boards or first light point shall
Be included as primary points & remaining points of the same looping
shall be considered as Secondary points and shall be counted in nos.
10) Circuit Wiring from DB to Kitchen Power points shall be measured in running meters
1 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included. (Normal Light) Average point length of primary & secondary to be derived by Contractor, from the drawing provided AND +/- 1 Mtr Measured Radially.
a) | Primary Light points controlled by MCB (1R 3Cx 2.5 sqmm wire) | Nos. | 0
b) | Secondary Light points looped in the same circuit. (1R 3Cx 2.5 sqmm wire) | Nos. | 0
1 | Supply, installation, testing & commissioning of point wiring for EMER light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included.(Emg. Light) Average point length of primary & secondary to be derived by Contractor, from the drawing provided AND +/- 1 Mtr Measured Radially.
a) | Primary Light points controlled by MCB (1R 3Cx 2.5 sqmm wire) | Nos. | 0
b) | Secondary Light points looped in the same circuit. (1R 3Cx 2.5 sqmm wire) | Nos. | 0
2 | Supply, installation, testing & commissioning of point wiring for light Point points, power points. Point wiring for primary point shall include wiring from Switch Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same switch board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits, 6A switch & switch board and accessories shall be included.
a) | Primary Light/Fan points controlled by Switch (1R 3Cx 2.5 sqmm wire) | Nos. | 15
b) | Secondary Light/Fan points looped in the same circuit. (1R 3Cx 2.5 sqmm wire) | Nos. | 22
c) | DB to SB & SB to SB circuit wiring : Wiring for switch board controlled by MCB already installed in DB by using 3 X 2.5 sq. mm flexible FRLSH copper wires in 25mm rigid GI conduits as per IS 9537 part-3 or surface mounted. | Mtrs | 80
5 | Providing point wiring for a cluster of 2 nos.6 amps socket outlets and 1 no. 16A switch/pop up box for Computer / POS Power Points using 3Cx4 sq. mm PVC insulated copper conductor wires from UPSDB to plug point in Existing Floor Raceway & GI Conduits as specified and then in flexible GI Conduits. (maximum 4 nos. clusters shall be connected on one circuit) switch and sockets to be mounted on front plate on partitions of furniture on hot dipped GI boxes concealed in wall 16A single pole plate switch with interconnections complete as per final approval of Architect/Consultant. (Cost of GI Conduit included and switch sockets are considered elsewhere). (Wires shall be FRLSH type) Average point length of primary & secondary to be derived by Contractor, from the drawing provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | Nos. | 1
b) | Secondary points | Nos. | 1
7 | Providing point wiring for Raw Power / points 1no. 6/16A switch socket outlet on Skirting level to be looped from the nearest point using 3Cx4 sq. mm copper conductor wires . (Cost of GI Conduit is included and switch sockets are considered elsewhere). (Wires shall be FRLSH type) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | Nos. | 15
b) | Secondary points | Nos. | 14
8 | Providing point wiring for Raw Power points 1no. 6A switch socket outlet on Skirting level to be looped from the nearest point using 3Cx4sq. mm copper conductor wires (Cost of GI Conduit is included and switch sockets are considered elsewhere). (Wires shall be FRLSH type) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | Nos. | 10
b) | Secondary points | Nos. | 10
10 | Providing point wiring for Primary & Secondary CCTV points using 3Cx4 sq. mm PVC insulated copper flexible FRLSH cable in already laid 25 mm dia. GI conduit surface mounted on ceiling, concealed in wall and or through partitions with necessary boxes / pull boxes, complete as per the final approval of Architect / Consultant ( Wires shall be FRLSH type ) | Mtr. | 10
11 | Supply and laying of following PVC insulated copper conductor 1100 volt grade stranded flexible FRLS wire in already laid GI conduit concealed or surface mounted making connections where ever required to complete the installation.(For Kitchen Power Points)
a) | 3Cx4 Sqmm Cu. Wires | Mtr. | 300
b) | 4R x 4Sqmm + 1R x 2.5Sqmm Cu. Wires | Mtr. | 10
12 | Supply & installation of 25 mm dia. GI conduit with pull box / junction box & all accessories for Kitchen & Bar Power wiring as per the requirement
a | - do - but conduit pipe shall be Rigid type. | Mtr. | 150
b | - do - but flexible conduit pipe | Mtr. | 20
13 | Supply & installation of 20 mm dia. GI conduit with pull box / junction box & all accessories for Lighting & Power wiring as per the requirement
a | - do - but conduit pipe shall be Rigid type. | Mtr. | 50
14 | Supply and installation of Perforated Cable Tray (ASIAN)out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant/Architect
a | 300 x 50 x 2mm | Mtr. | 20
c | 150 x 50 x 2mm | Mtr. | 30
15 | Supply and installation of GI trunking (SV POWER/ASIAN) with 2 mm thickness & properties/clamps for suspension at appropriate intervals & as per the route approved by Architect/Consultant. (For DATA/CONTROL WIRING/LIGHTING & POWER CIRCUITS / KITCHEN)
e | 50 x 50 x 2mm | Mtr. | 20
16 | Supply and installation of GI raceway with 2 mm thickness & proper ties/clamps at appropriate intervals & as per the route approved by Architect/Consultant. (Cost of cutting the floor for laying of raceways to be included).
c | 1 runs of underfloor GI raceways of size 100 x 40 mm | Mtr. | 20
17 | Supply & installation of GI junction boxes with 2 mm thickness, 2mm thick SS cover with 2” extra on all sides SS cover on top and having screw fixed plates on all four sides with knock out holes for conduits. The plates shall be retained on the sidezs having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be prepared as per the final approval of Architect/Consultant. The junction boxes shall be protected from the entry of unwanted material till the completion of the project & the SS plates shall be installed after the final polishing of flooring.
d | suitable for 150 x 150 x 50 mm | Nos. | 3
18 | Supply, installation, testing & commissioning of flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect/Consultant
a | 6A one way plate type switch | Nos. | 20
b | 6A 5 pin Socket outlet | Nos. | 2
c | 6A 5pin switch socket outlet for CCTV & Charging point | Nos. | 12
d | 2 nos 6A switch socket outlet | Nos. | 2
f | 1 nos. 6/16A socket controlled by1nos 6/16A switch for Kitchen | Nos. | 25
h | Data Socket (D-Link) | Nos. | 10
i | Telephone Socket | Nos. | 2
j | TV Socket | Nos. | 4
16 | Supply, installation of temporary lighting & power arrangement for construction purpose of with industrial type switch & sockets/MCB's/ELCB's & lighting fittings as required to finish the work for interior contractor & necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules & regulations as per Airport Security Department. The material shall be taken back by the contractor. | Job | 1
1 | 22 W DOWN LIGHT | Nos. | 32
4 | TUBE LIGHT | Nos. | 2
VII | EARTHING
3 | Supply & erection of G.I. strip of 25 x 3 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | Mtr. | 60
5 | Supplying & erecting bare copper conductor of 8 swg for earthing purpose | Mtr. | 40
9 | Supplying & installation testing & commissioning of earth terminal box | Nos. | 1
VIII | MISCELLANEOUS
1 | Supply & Installation of 6A 3 pin plug top | Nos. | 4
2 | Supply & Installation of 16A 3 pin plug top | Nos. | 8
4 | Supply & laying of Rubber Mats, CPRI tested conforming to standards like BS 921, ASTM-D 178 & IEC 479 for different operatng voltage ratings as below.
7 | Supply & fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language | Nos. | 1
A | DATA AND TELEPHONE SYSTEM
1 | Supply & Installation of 25mm.dia. HMS GI conduit with pull box/ junction box & all accessories for DATA /VOICE/WIFI wiring as per the requirement. | Mtr. | 150
2 | Supply & Installation of Cat-6 E Cable in above conduits for DATA System. | Mtr. | 200