## FIRE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | IN_HYD_FF018_CARLSJR |  |  | DATE: | 2024-05-02
|  |  |  | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire, and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | Provisional Sum
B | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
B.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangement with ceiling / wall etc. (Make: Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent with airport approval)
B.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 12
B.1.2 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 4
B.1.3 | Upright Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 15
FIRE SPRINKLER PIPE VALVES & ACCESSORIES
B.2 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.)
B.2.1 | 65 mm Dia | Nos | 1
B.3 | Supply, Installation, Testing & Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem & lever, with necessary weldable fittings in position as per drawings / site conditions. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.)
B.3.1 | 25 mm Dia | Nos | 1
B.4 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. (Make: Potter/ System Sensor or equivalent with airport approval)
B.4.1 | 65 mm Dia | Nos | 1
FIRE SPRINKLER PIPING
B.5 | Supply, Installation, Testing & Commissioning of MS "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) (Make: HSL, Mukut, Lalit steel or equivalent)
B.5.1 | 25 mm Dia | Mtr | 53
B.5.2 | 32 mm Dia | Mtr | 10
B.5.3 | 40 mm Dia | Mtr | 6
B.5.4 | 50 mm Dia | Mtr | 4
B.5.5 | 65 mm Dia | Mtr | 14
GRANT TOTAL
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.