## HVAC
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | IN_HYD_FF018_CARLSJR |  |  | DATE: | 2024-05-02
|  |  |  | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire, and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | Provisional Sum
B | HVAC EQUIPMENTS
AC EQUIPMENT (CHILLED WATER - TYPE)
B.1 | Supply, installation, testing and commissioning of chilled water type High static Fan coil unit of approved make comprises with evaporator coil, high efficiency fan-motor assembly, 4RD chilled water cooling coil section, pre-filters with EU3/G4 class filters, condensate drain pan (SS 18G) duly insulated with cross linked polymer, insulated drain piping; Units shall be equipped with valve package comprises of ball valve with strainer on the inlet side and PICV with two isolation ball valves on the outlet side. The unit shall be suitable for 230 ± 10 volts, 50/60 Hz, 1 phase AC supply with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. Fan coil units shall be selected for the lowest operating noise level.
B1.1 | 5.5 TR - (2200 CFM @ 90-100 PASCAL -ESP) | Nos | 1
AIR CLEANING EQUIPMENTS
B.2 | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Electrostatic Precipitator(ESP) of approved make with minimum 25 mm thick panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate .The Unit shall be suitable for 230V, 1 Phase, 50/60 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above.
B.2.1 | 3600 CFM | Nos | 1
C | AC PIPING AND ACCESSORIES
AC CONDENSATE DRAIN PIPE
C.1 | Supply, installation and testing of Rigid PVC condensate drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape.
C.1.1 | 25 mm Ø | Mtr | 7
AC CHILLED WATER PIPING
C.2 | Supply, installation and testing of MS class (C) Pre-Insulated Chilled Water Pipe of approved make with expanded polyurethane foam (PUF) insulation of 36 kg/m3 minimum density, thickness as specified below and 26 G aluminum cladding with supports and all fittings such as bends, tees, elbows, reducers, flanges, special fittings, suspension hangers, supports as applicable as per site conditions. The insulation shall completely fill the annular space between service pipe and jacket and shall be bonded to both by Cold adhesive. Rubber saddles shall be considered below supports for all the piping works.
C.2.1 | 32 mm Ø - (Insulation - 30 mm thick) | Nos | 30
D | AC PIPING VALVES & ACCESSORIES
D.1 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements.
D.1.1 | Dial Size - 63 mm Ø | Nos | 2
D.2 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements.
D.2.1 | Dial Size - 63 mm Ø | Nos | 2
E | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
E.1 | Supply, installation and testing of Galvanized Iron (GI)/ Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square / Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
E.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 75
E.1.2 | 22 Gauge - (0.85 mm Thick) - Supply Air Duct | Sq.mtr | 3
E.1.3 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.mtr | 33
E.2 | Supply, installation and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
E.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | Sq.mtr | 42
DUCT ACCESS DOORS
E.3 | Supply, installation, and testing of Hinged type Duct Access Doors as per drawings and to allow easy and convenient access to equipment or any other component within ductwork with all necessary fittings, accessories and airtight gaskets etc.
E.3.1 | 250 mm X 250 mm - (MS) | Nos | 4
E.4 | Supply, installation, and testing of Insulated Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by air handling units or any other equipment's connected to the duct with air tight fittings with all necessary accessories.
E.4.1 | For FCU | Nos | 1
F | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS & ACCOUSTIC LINNINGS
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
F.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6, Black Colour with silver foil covering with having a density of 50 ± 5 Kg/M3. Quote shall be inclusive of necessary Adhesive.
F.1.1 | 19 mm thicknesses - (SAD) | Sq.mtr | 78
F.1.2 | 19 mm thicknesses - (MUAD) | Sq.mtr | 33
F.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using rockwool with silver foil covering, density of 50 Kg/m3.Quoute shall be inclusive of necessary Adhesive.
F.2.1 | 50 mm thicknesses - (KEAD) - For Kitchen Exhaust | Sq.mtr | 42
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
F.3 | Supply, installation of Acoustic Lining of approved makes for duct insulation using open cell processed elastomeric nitrile rubber, with having a density of 150 ± 10 Kg/m3 Quote shall be inclusive of necessary Adhesive.
F.3.1 | 15 mm thicknesses - (SAD) | Sq.mtr | 4
G | AIR DISTRIBUTION DUCT - DAMPERS
DUCT AIR CONTROL DAMPERS
G.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper / Collar Damper of approved make.
G.1.1 | Size - 600 x 100 mm | Nos | 7
G.1.2 | Size - 450 x 450 mm | Nos | 4
G.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square / Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.
G.2.1 | Size - 600 x 200 mm | Nos | 1
G.2.2 | Size - 450 x 200 mm | Nos | 1
G.2.3 | Size - 500 x 300 mm | Nos | 1
G.2.4 | Size - 500 x 150 mm | Nos | 1
G.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square / Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.(For Kitchen Exhaust MS duct)
G.3.1 | Size - 700 x 400 mm | Nos | 1
G.3.2 | Size - 500 x 300 mm | Nos | 1
G.3.3 | Size - 450 x 250 mm | Nos | 1
G.3.4 | Size - 400 x 200 mm | Nos | 2
H | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
H.1 | Supply, installation, testing and commissioning of Extruded Aluminium Linear Bar Grille of approved make with fixed Aerofoil blades 15° deflection with frame of 20mm flange with all necessary fixing arrangements. powder coated finish with RAL Colour as required by ID Designer / Architect.
H.1.1 | Neck Size - 100 mm X 600 mm - (1 - Way) | Nos | 2
H.1.2 | Neck Size - 100 mm X 600 mm - (2 - Way) | Nos | 5
H.2 | Supply, installation, testing and commissioning of Extruded Aluminium Non Vision Door Transfer Grille of approved make with Inverted V type blade to avoid see through Cision and both side frame which can be adjusted to varying door thickness with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
H.2.1 | 250 mm X 250 mm | Nos | 1
DIFFUSERS
H.3 | Supply, installation, testing and commissioning of Extruded Aluminium Square Ceiling Diffuser of approved make with Four way throw with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
H.3.1 | Neck Size - 450 mm X 450 mm (Outer Size - 595 mm X 595 mm) - Tegular | Nos | 7
HVAC SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
H.4 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
H.4.1 | Labelling & Tagging for Services and Equipment's | Lot | 1
TESTING AND BALANCING
H.5 | Air balancing of Supply, Fresh air and Exhaust air system to arrive as per design air flow rates | Lumpsum
H.6 | Water balancing of Entire Chilled Water piping system to arrive the designed flow rates. | Lumpsum
H.7 | Chilled water pipe Pressure testing at 15kgf/cm2 hydrostatics pressure for a minimum 24hrs hold time .Testing should be done in the presence of Airport Concerned Persons. | Lumpsum
SHOP DRAWINGS & APPROVALS
H.8 | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, Fire along and Gas system, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. | Lumpsum
MISCELLANEOUS OR ANY ADDITIONAL ITEMS
H.9 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
H.9.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 1
H.9.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 1
H.9.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 1
GRAND TOTAL
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## ELEC
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | IN-HYD-FF018-CARLSJR |  |  | DATE: | 02.05.24
|  |  |  | REV: | R0
ELECTRICAL SERVICES, CCTV & DATA - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
Item Code | Item Name | UOM | Qty | UNIT COST | REMARKS
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | Provisional Sum
A | METER / METER PANEL
A.1 | Supply, Installation, Testing & Commissioning of kWH / MFM Energy Meter Panel complete with Enclosure (If required as per site condition / Airport TDM). Energy Meter shall be of Digital kVAH Type and Make / Manufacturer from below list, or any other make with kVAH option with Approval from TS Department. For Make refer list below, Single Phase (For load below 40A) : Make - MID (Algodue Electronica), Model - UEM 40-2C. Type - Direct. Three Phase (For load below 60A) : Make - Secure, Model - Sprint 350, Type - Direct. Three Phase (For load above 60A) : 1) Make - Secure, Model - Elite 445, Type - C.T. 2) Make - Conzerv (Schneider Electric), Model - EM6438, Type - C.T. 3) Make - L & T, Model - Vega TM (WDM303FDWA1), Type - C.T.
A.1.1 | 250A/5A ENERGY METER (CT TYPE) | Nos. | 1
B | LV CABLING
B.1 | Supply, Installation, Testing & Commissioning of Fire Rated LS/LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape / Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD / Load Calculation Sheet (Main Cable) & Unarmoured Single Core Wire (ECC), complete with Termination of the same with Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground / on Cable Tray / through Cable Trunking / in Pipe / on Wall / Trench as required. Make : Electrical Wires & Cables : Finolex, Polycab, RR Kables, KEI or equivalent. For cables laid on Cable Tray / in Pipe / on Wall / Trench - the rate shall include necessary supporting / clamping arrangements.
B.1.1 | 4R x 95 SQ.MM | Mtr. | 20
B.1.3 | 4R x 35 SQ.MM | Mtr. | 10
B.1.5 | 4R x 6 SQ.MM | Mtr. | 10
B.1.6 | 4R x 4 SQ.MM | Mtr. | 20
B.1.7 | 1C x 35 SQ.MM | Mtr. | 20
B.1.7 | 1C x 16 SQ.MM | Mtr. | 10
B.1.8 | 1C x 6 SQ.MM | Mtr. | 20
B.1.9 | 1C x 4 SQ.MM | Mtr. | 20
C | DISTRIBUTION BOARDS
C.1 | Supply, Installation, Testing & Commissioning of Surface / Flush mounting 10kA / 25kA (As per Panel requirement) Distribution Boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate & knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring & earth bus on insulation mount. Make : Electrical Panel / DB's & Breakers (MCB, RCBO, ELCB & MCCB) : Legrand, Siemens, ABB, Schneider or equivalent. All DB's must named as per the SLD / Load Calculation Sheet. Laminated SLD & Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB / RCBO shall be Hpi / Si series & MCB's shall be 'B" / 'C' Curve (As per requirement).
SMDB
C.1.1 | 10Way TPN Panel Board with 250A 4P MCCB incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
LPDB
C.1.2 | 16Way TPN Panel Board with 125A 30 mA 4 P RCBO incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
UPS DB
C.1.3 | 6 Way SPN Panel Board with 20A 30 mA 2P RCBO incomer and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
D | LIGHT FIXTURES POINT WIRING
D.1 | Supply, Installation, Testing & Commissioning of Light Fixture Point wiring (Light Fixtures to be as approved by Architect Design & BOQ) with Lamps, Ballasts / Drivers / Starters, Switches / Lighting Control Switch Board with Fire Rated LS/LSZH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Light Fixtures : Philips, Wipro, Crompton, Syska or equivalent. Make : PVC Conduits : Sudhakar, Shakti or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
D.1.1 | CEILING LAMP (Point Wiring only) | Nos. | 4
D.1.2 | CEILING LAMP (Point Wiring only) | Nos. | 3
D.1.3 | DOWN LIGHT (Point Wiring only) | Nos. | 55
D.1.4 | 600 X 600MM LED PANEL LIGHT(Point Wiring only) | Nos. | 13
D.1.5 | TRACK LIGHT BLACK FINISH (600X600MM) (Point Wiring only) | Nos. | 5
D.1.6 | LED STRIP LIGHT WITH DIFFUSER(Point Wiring only) | Nos. | 1
D.1.8 | INDICATIVE LOCATION OF SUSPENDED LIT SIGNAGE(Point Wiring only) | Nos. | 1
D.1.7 | INDICATIVE SIGNAGE (Point Wiring only) | Nos. | 6
D.1.8 | Lighting Control Switch board with switches as required (Point Wiring only) | Nos. | 1
D.1.9 | EXIT LIGHT (Wall / Ceiling Mounted) | Nos. | 3
E | WIRING DEVICES (SWITCHES & SOCKETS)
E.1 | Supply, Installation, Testing & Commissioning of Wiring Devices (Switches & Sockets - Face Plate Finish as approved by Architect / Matching to Architecture Finishes) with Fire Rated LS/LSZH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Switch & Sockets : Anchor Roma / Penta, Legrand, Havells Crabtree, Finolex, L & T Switchgear or equivalent. Make : PVC Conduits : Sudhakar, Shakti or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
E.1.1 | 13A SINGLE SWITCHED SOCKET OUTLET | Nos. | 18
E.1.2 | 13A DUAL SWITCHED SOCKET OUTLET | Nos. | 9
E.1.4 | 13A DUAL SWITCHED SOCKET OUTLET + DUAL USB PORT | Nos. | 5
E.1.5 | 16A SINGLE SWITCHED SOCKET OUTLET | Nos. | 12
E.1.6 | 16A SINGLE SWITCHED METAL CLAD SOCKET OUTLET | Nos. | 19
E.1.7 | 20A SINGLE SWITCHED METAL CLAD SOCKET OUTLET | Nos. | 1
E.1.8 | 20A SINGLE SWITCHED METAL CLAD SOCKET OUTLET | Nos. | 1
E.1.9 | 16A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 1
E.1.9 | 20A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 1
E.1.10 | 20A DOUBLE POLE SWITCH WITH NEON INDICATOR | Nos. | 1
E.1.10 | 16A DOUBLE POLE SWITCH WITH NEON INDICATOR | Nos. | 1
E.1.11 | 20A SINGLE SWITCHED SOCKET OUTLET | Nos. | 1
E.1.13 | 63A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 1
E.1.14 | 32A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 4
F | CONTAINMENT (CABLE TRAY & TRUNKING)
F.1 | Supply & Installation of GI Cable Tray & GI Cable Trunking, through Wall / Ceiling / Floor as per drawings, complete with standard accessories / factory made fittings, earthing throughout the run with copper braids, wall / ceiling suspended supports, etc. Make : Cable Management System : Dudhat, Super, K.R. Power supports or equivalent with Airport approval.
F.1.1 | 100 x 100 MM CABLE TRUNKING | Mtr. | 9
F.1.1 | 75 x 75 MM CABLE TRUNKING | Mtr. | 9
F.1.2 | 50 x 50 MM CABLE TRUNKING | Mtr. | 18
G | UPS SYSTEM
G.1 | Supply, Installation, Testing & Commissioning of UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) & standard accessories / equipments required for complete functioning of the system, earthing, support system (if required), etc. Make : UPS System : Luminous, APC, Microtek or equivalent with Airport approval.
G.1.1 | 3 KVA Single phase UPS with 30 Minute Back-up | Nos. | 1
H | CCTV SYSTEM
H.1 | Supply, Installation, Testing & Commissioning of CCTV System with suitable / required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console / DVR, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make : CCTV System : Hikvision, Honeywell, Dahua, or equivalent with Airport approval. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
H.1.1 | CCTV Dome Camera, 4 Megapixel / As approved or confirmed by client, Real Day / Night, Exir, IR LED, IP 67, with all neccessary accessories, Power supply units etc. | Nos. | 6
H.1.2 | CCTV IP Dome Camera (CAT 6), 4 Megapixel / As approved or confirmed by client, Real Day / Night, Exir, IR LED, IP 67 with all neccessary accessories, Power supply units etc. | Nos. | 1
H.1.3 | DVR with 45 Days Back-up | Nos. | 1
I | DATA NETWORK SYSTEM
I.1 | Supply, Installation, Testing & Commissioning of Data & Telephone Network System with required cabling through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make : IT Cables & Accessories : Belden (Part Code - 7834ANC). The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
I.1.1 | Dual Data outlet (RJ45) Jack | Nos. | 5
I.1.2 | Single Data outlet (RJ45) | Nos. | 6
I.1.3 | Patch Cords (1.5 meters length) | Nos. | 17
GRAND TOTAL NET
NOTE : The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## PHE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | IN_HYD_FF018_CARLSJR |  |  | DATE: | 2024-05-02
|  |  |  | REV: | R0
PLUMBING SYSTEM - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
| If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | Provisional Sum
B | DRAINAGE SYSTEM
INTERCEPTORS & SEPERATORS
B.1 | Supplying, Installing, Testing & Commissioning of Greese Trap or Grease Interceptor (Above Ground / floor) of 304 grade stainless steel material with interceptor body, preforated bucket, baffles, integral trap, inlet & outlep pipe sleeve and stainless steel interceptor cover of approved make and with all necessary fittings & connectors etc. (Make : Nugreen , Kessel and Concessionaire can propose another make in SS material.)
B.1.1 | NGT 50 - Flow Rate (2.20 LPS / 132 LPM) | Nos | 1
VALVES & ACCESSORIES
B.2 | Supplying, Installing, Testing & Commissioning of ABS Air Admittance Valve conforming to EN 12380, with an air admittance air flow rate of 6.1 L/s and a temperature range of operation from -20 C to + 60 C of approved make with all necessary adapters, fittings and connectors etc. (Make : Astral/Supreme for Pipe and Fittings)
B.2.1 | 32 mm Dia | Nos | 1
DRAINS, TRAPS & CLEANOUTS
B.4 | Supplying, Installing, and testing of AISI 304 grade Stainless Steel Floor Drain with top square anti-slip mesh grating drain cover of 350 X 350 mm, lateral/horizontal outlet, with removable waste basket, odor water seal trap of approved make with all necessary adapters, fittings, and connectors etc. (Make : Custom made)
B.4.1 | 50 mm Dia - Outlet | Nos | 4
B.5 | Supplying, Installing, and testing of uPVC 'P' Trap (self-cleaning type) with odor water seal trap of approved make with all necessary adapters, fittings and connectors, etc.
B.5.1 | 32 mm Dia Outlet | Nos | 6
B.6 | Supplying, Installing & Testing of cast iron Floor Trap (150 mmx 150 mm) with Stainless Steel slotted top cover, odour water seal trap of approved make with all necessary adapters, fittings and connectors etc. (Makes : NECO or equivalent with Airport approval)
B.6.1 | 75 mm Dia - Outlet | Nos | 1
DRAINAGE SYSTEMS PIPING
B.7 | Supplying, Installing, Testing, and Commissioning of uPVC Pipe, for drainage with all necessary fittings such as bends, wye's, reducers, san tee's, double wye's, double combinations, san cross, and cleanout plugs etc, of approved make. and with all necessary supports/clamps for the above-raised floor pipes as per standards and site conditions/requirements. (Make : Astral/Supreme for Pipe and Fittings)
B.7.1 | 32 mm Dia | Mtr | 2
B.7.2 | 40 mm Dia | Mtr | 10
B.7.3 | 50 mm Dia | Mtr | 25
B.7.4 | 75 mm Dia | Mtr | 6
C | WATER SUPPLY SYSTEM
WATER SUPPLY EQUIPMENTS
C.1 | Supply, Installation, Testing & Commissioning of Electric Water Heater with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. and proper supports necessary as per standards and site condition / requirements. (Make : Ariston/Racold or equivalent with Airport approval)
C.1.1 | 65 Liters vertical storage water heater | Nos | 1
C.2 | Supply, Installation, Testing & Commissioning of RO Filteration Unit for supplying pure filtered potable water to equipments like Combi-steamers & baking ovens, Fresh water taps & Coolers, Coffee/ Espresso machines, Dish-washers, Post-mix machines, Ice-machines, and Boiling-water taps etc. with necessary prefilters, filter cartridges, manifold heads, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. Final make, model and details to be finalized by specialist vendor after examining the water test report of incoming water supply provided at site. (Make : Eco Smart/Livpure or equivalent with Airport approval)
C.2.1 | 15 Ltrs / Hr - Flow Rate | Nos | 1
WATER SUPPLY PIPE VALVES & ACCESSORIES
C.3 | Supply, Installation, Testing & Commissioning of Brass Ball Valve with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar of approved make and with all necessary fittings. (Makes : NECO or equivalent with Airport approval)
C.3.1 | 25 mm Dia | Nos | 2
C.4 | Supply, Installation, Testing, and Commissioning of chrome plated Angle Valve with wall flange/rosette for all plumbing equipment/fixtures with a pressure rating of 16 Bar of approved make and with all necessary fittings. Including making good the wall/partition as per Architectural / Interior Design and as per relevant standards. (Makes : NECO or equivalent with Airport approval)
C.4.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 21
COLD WATER SUPPLY PIPING
C.5 | Supply, Installation, Testing & Commissioning of (Chlorinated Poly Vinyl Chloride) CPVC Pipe conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Astral/Supreme for Pipe and Fittings)
C.5.1 | 15 mm Dia | Mtr | 16
C.5.2 | 20 mm Dia | Mtr | 10
C.5.3 | 25 mm Dia | Mtr | 13
C.6 | Supply, Installation, Testing & Commissioning of Copper Pipe conforming to BS 2871 / EN 1057, (continous operating temperature range of maximum 90°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Manibhadra fittings or equivalent with Airport approval)
C.6.1 | 15 mm Dia | Mtr | 10
C.6.2 | 22 mm Dia | Mtr | 12
PIPING THERMAL INSULATION
C.7 | Supply & fixing of Pipe Insulation of 13 mm thick, with Polyethylene-based, closed-cell foam pipe insulation and polymer protective coating to prevent external mechanical damage of approved make for Hot water pipe with a operating temperature range of 0°C to 100°C, Thermal conductivity (λ) 0.038 W/m-K @ 40°C including suitable adhesives to fix the insulation to pipe. (Make : Thermax, Maxima, Fuelpac or equivalent)
C.7.1 | 15 mm Dia | Mtr | 10
C.7.2 | 22 mm Dia | Mtr | 12
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## FIRE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | IN_HYD_FF018_CARLSJR |  |  | DATE: | 2024-05-02
|  |  |  | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire, and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | Provisional Sum
B | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
B.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangement with ceiling / wall etc. (Make: Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent with airport approval)
B.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 12
B.1.2 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 4
B.1.3 | Upright Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 15
FIRE SPRINKLER PIPE VALVES & ACCESSORIES
B.2 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.)
B.2.1 | 65 mm Dia | Nos | 1
B.3 | Supply, Installation, Testing & Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem & lever, with necessary weldable fittings in position as per drawings / site conditions. (Make: Tyco/Viking/Victualic/ HD fire/Newage or equivalent with airport approval.)
B.3.1 | 25 mm Dia | Nos | 1
B.4 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. (Make: Potter/ System Sensor or equivalent with airport approval)
B.4.1 | 65 mm Dia | Nos | 1
FIRE SPRINKLER PIPING
B.5 | Supply, Installation, Testing & Commissioning of MS "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) (Make: HSL, Mukut, Lalit steel or equivalent)
B.5.1 | 25 mm Dia | Mtr | 53
B.5.2 | 32 mm Dia | Mtr | 10
B.5.3 | 40 mm Dia | Mtr | 6
B.5.4 | 50 mm Dia | Mtr | 4
B.5.5 | 65 mm Dia | Mtr | 14
C | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE )
FIRE ALARM SYSTEM - DETECTION DEVICES
C.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke & Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles with all necessary mounting and fixing arrangements. (Above & Below Ceiling) Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
C.1.1 | Below ceiling level | Nos | 3
C.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles with all necessary mounting and fixing arrangements. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
C.2.1 | Heat Detector - 58°C fixed temperature | Nos | 2
C.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
C.3.1 | Manual Call Point - (Wall / Partition Mounted) | Nos | 1
C.4 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator & and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB / EN54 along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
C.4.1 | Sounder Strobe - (Wall / Partition Mounted) | Nos | 1
FIRE ALARM SYSTEM - MODULE DEVICES
C.5 | Supply, Installation, Testing, and Commissioning of Addressable Type Monitor Module along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
C.5.1 | Monitor Module | Nos | 2
C.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Control Module for shutting down FCU’s, and magnetic fire door holders. Elevator recall, fire damper, pressurisation fan, strobes etc along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
C.6.1 | Control Module | Nos | 1
C.7 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolation Module along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles. Make Fire Alarm Devices: Johnson or as directed by the Airport. Make: PVC Conduits: Sudhakar, Shakti or equivalent
C.7.1 | Isolation Module | Nos | 1
D | FIRE EXTINGUISHERS
D.1 | DRY POWDER STORED FIRE EXTINGUISHER
D.1.1 | Supply and fixing of 4.0 Kg ABC Dry Powder (Stored Pressure) Type Fire Extinguisher. pressurized with dry nitrogen gas at 15 bar. Design, construction and testing as per IS 15683 with BIS Fire rating 2A : 21B, Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 3
D.2 | CO2 PORTABLE FIRE EXTINGUISHER
D.2.1 | Supply and fixing of 3.0 Kg CO2 (Carbon-dioxide) Type Fire Extinguisher. Design, construction and testing as per IS 15683 with BIS Fire rating 21B, Body Hydrotested at 250 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 3
D.3 | FIRE EXTINGUISHER MOUNTING BRACKET / MOUNTING STAND
D.3.1 | Supply and fixing of Mounting Bracket / Stand for Fire Extinguishers fabricated out of good quality M.S, Pipe / Plate & Fittings duly painted with primer and final enamel paint coat as per the regulatory authority or to match with the ID design to suit the above Fire Extinguishers. (Make:Kanex or as recommended by GHIAL-ARFF) | Nos | 6
GRANT TOTAL
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.