## HVAC
Dominos ………………….Civil & Interiors BOQ¦ Ver 3.0
1. Partition, Panelling - Sq. Ft area – one side only
2. Storage Units - Sq. Ft area – Front elevation length x Front Finished height
3. False Ceiling - Sq. Ft area – Flat surface area in reflected ceiling plan
4. Flooring - Sq. Ft. area – Internal area contained within skirting
5. Pls Note Only Bison , Marine Ply and Wpc Board to be used instead of Commercial Ply
6. Chiseling work included in the items or else specified
7. Scaffolding will be in contractor scope upto 4mtr & Above 4mtr rate will be chargeable. If required for installation of civil & MEP.
8. All Items Rates are inclusive of material lead & lift charges.
A. CIVIL & INTERIOR BOQ-Ahemedabad Airport |  |  |  |  | Area | 600
Task No. |  | Sub Task No. | Name of Item | Description of Item | Unit | Quantity | Rate | Amount | Remark
| H.4.0 |  |  | Exhaust Fan for Toilet supply
|  | a.1 |  | Supplying and erecting fresh air cum Exhaust fan of light duty 250 V A.C. 50 cycles 300mm/400mm. 1400 RPM rust proof body & blades, wiremesh, duly erected in an approved manner.(Havells/Usha/Crompton or Orient.) | Each | 1 |  | 0
|  | a.2 |  | Heavy Duty 450 mm Dia Exhaust Fan (Make Cromptoon & Equivalent) | Each | 1 |  | 0
Sub Total of H.4.0 | [7 empty] | 0
| H.5.0 |  |  | Additional HVAC Items
|  | a |  | INSULATED DRAIN PIPING
SITC of PVC drain piping with 9mm thick tubular insulation complete with PVC, fitting, accessories etc.
|  | a.1 |  | 25mm dia | Rmt. | 20 |  | 0
|  | a.2 |  | 32mm dia | Rmt. | 10 |  | 0
0
|  | b |  | Supply, Installation, Testing & Commissioning of Chilled water Hi-wall / Cassette units complete with cooling coil, centrifugal blower, drive set & motor, cordless remote control etc. |  |  |  | 0
|  | b.2 |  | 2.0TR CHW Hi-wall | Nos. | 3 |  | 0
|  | b.3 |  | 1.5TR CHW Hi-wall | Nos. | 2 |  | 0
|  | b.4 |  | SITC of Hiwall / Cassette unit shall be factory fitted with valve package comprising of 2 way motorized valve with Cooling Thermostat for various chilled water units, ball valve with 'Y' strainer at inlet & ball valve at outlet and necessary copper coil piping connections. | Sets | 5 |  | 0
0
|  | c |  | Chilled water piping MS `C' class with 25mm thick Nitrile Rubbe insulation. |  |  |  | 0
|  | c.2 |  | 40 mm dia. | Rmt | 5 |  | 0
|  | c.3 |  | 32 mm dia. | Rmt | 5 |  | 0
|  | c.4 |  | 25 mm dia. | Rmt | 40 |  | 0
0
|  | e |  | Butterfly Valve (with insulation). |  |  |  | 0
|  | e.1 |  | 40 mm dia | Nos. | 4 |  | 0
0
0
|  | g |  | Power / Control Cabling (Max. 5 Rmt.) between Units and 3-way valve. | Sets | 5 |  | 0
|  | g.1 |  | (Any extra length shall be payable @Rs. 300/- per Rmt.) |  |  |  | 0
|  | h |  | EXHAUST AIR FAN (MAKE: KRUGER/ NICOTRA/EQUIVALENT)
SISW Cabinet Type Fan For Kitchen Hood Exhaust : Supply, installation, testing & commissioning of - SISW cabinet type fan to be installed on Terrace(location will be confirm) for exhaust air from Kitchen Hood to outside, Floor Mounted /Ceiling suspended SISW cabinet type centrifugal fan for exhaust system complete without starter panel (Should be installed within 5Rft Distance from unit), control cable IP-55 TEFC motor with copper winding, Direct driven/ Belt driven centrifugal blower, VCD & flexible connection at fan outlet and vibration isolator. Outlet velocity of fan shall not exceed 10 m/s and fan motor speed not exceed Fan should be VFD compatible. (Note : Power Cabling up to Starter Panel will be in scope of Client / Electrical Vendor).
|  | h.2 |  | 2800 CFM, SP: 30 mm WG (Suction) | Nos. | 1 |  | 0
|  | i |  | FRESH AIR FAN (MAKE: KRUGER/ NICOTRA/EQUIVALENT)
DIDW Cabinet Type Fan For Fresh Air : Supply, installation, testing & commissioning of - DIDW cabinet type fresh air fan to be installed for Kitchen Hood, ceiling suspended DIDW cabinet type centrifugal fan with copper winding for fresh system complete with 10 micron prefilter, Including Necessary cabling from fan to socket. Outlet velocity of fan shall not exceed 10 m/s and fan motor speed not exceed Fan should be VFD compatible. (Note : Power Cabling up to Starter Panel will be in scope of Client / Electrical Vendor).
|  | i.2 |  | 2500 CFM, SP: 25 mm WG ESP | Nos. | 1 |  | 0
|  | j |  | STARTER PANEL FOR EXHAUST AIR & FRESH AIR FAN
|  | j.1 |  | Supply, Fabrication, Installation, Testing & Commissioning of HVAC sarter panel for kitchen exhaust fans (As given above) with IP-55 Enclosure comprising of main incoming feeder, 1 nos. of DOL 3-phase starter for exhaust fans, 1 nos. of DOL 3- phase starter for fresh air fans, ON/OFF/Trip indicators, Start/Stop/ Push Buttons, Auto/Manual switch, Voltmeters , NO-NC contacts for integrating of fresh air fan with exhaust air fans, minimum 2 potential free contacts etc. Installation with necessary accessories and required wiring with termination, glanding, lugs comprising etc. | Nos. | 2 |  | 0
Sub Total of H.4.0 | [7 empty] | 0