## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
1.01 | Design, fabrication, assembling, wiring & supply, installation, testing & commissioning of Change over Panel, fabricated steel CRCA painted sheet steel. The boards shall be treated with all anticorrosive process before painting as per standards with final approved shade of powder coated as approved. 2 nos. Earthing terminals shall be provided for all panels. Boards shall be fabricated in length, height, depth etc. To match with site conditions.
a | 125A 4pole Change over Switch AUTO type | Unit
c | 200A 4pole Change over Switch AUTO type | Unit
d | 250A 4pole Change over Switch AUTO type | Unit
2 | SITC OF ENCLOSURES FOR MCB FOR OUTDOOR APPLICATION WITH MCB DP & FP
2.01 | DP MCB in weather proof enclosure with MCB
a | 40-63A | Nos | 2
b | 6-32A | Nos | 3
2.02 | 4 POLE MCB in weather proof enclosure with MCB
c | 6-32A | Nos | 1
3 | SITC OF INDUSTRIAL TYPE LE-GRAND METRA PLUG/TEMPRA PLUG FOR EQUIPMENT POWER CONNECTIONS WITH REQUIRED MCB
3.01 | 40A 5Pin 3 Phase Plug and Socket with TPN MCB | Nos. | 3
3.02 | 32A 5Pin 3 Phase Plug and Socket with TPN MCB | Nos | 2
3.03 | 32A 3Pin Single Phase Plug and Socket with SP MCB | Nos | 2
3.04 | 20A 3Pin SP Metal Clad Socket with SP MCB (Industrial Type) | Nos | 30
4 | CABLES, TRAYS & TERMINATIONS
4.01 | SITC of cables 1.1KV grade PVC/XLPE insulated armoured Aluminium/Copper conducter cables. The cables shall be laid as per drawings or on cable trays laid over MS supports, cable racks, or fixing on wall including clamping of cable, or in wall chases. Rate to include making good the wall chases with cement mortar.
b | 3 C X 2.5 sq. mm. CU PVC ARMOURED | Rmt | 100
c | 3 C X 4 sq. mm. CU PVC ARMOURED | Rmt | 80
d | 3 C X 6 sq. mm. CU PVC ARMOURED | Rmt | 40
e | 3 C X 6 sq. mm. CU PVC UNARMOURED | Rmt | 35
j | 4 C X 4 sq. mm. CU PVC ARMOURED | Rmt | 100
l | 4 C X 10 sq. mm. CU PVC ARMOURED | Rmt | 140
s | 3.5 C X120 sq. mm. AL. XLPE CABLE ARMOURED | Rmt | 45
4.02 | SITC of Cable Terminations including single/double compression chrome plated Brass glands and Copper lugs (crimping type). PVC taping as required with all accessories required, complete.
b | 3 C X 2.5 sq. mm. CU PVC ARMOURED | Nos | 8
c | 3 C X 4 sq. mm. CU PVC ARMOURED | Nos | 10
d | 3 C X 6 sq. mm. CU PVC ARMOURED | Nos | 4
e | 3 C X 6 sq. mm. CU PVC UNARMOURED | Nos | 4
j | 4 C X 4 sq. mm. CU PVC ARMOURED | Nos | 10
l | 4 C X 10 sq. mm. CU PVC ARMOURED | Nos | 8
s | 3.5 C X120 sq. mm. AL. XLPE CABLE ARMOURED | Nos | 2
t | 3.5 C X150 sq. mm. AL. XLPE CABLE ARMOURED
4.03 | SITC of prefabricated GI Perforated type 2MM THICK X 50MM HT. cable trays including Tees / Bends / Crossing / Reducers / Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as required including support at every 1500mm as required
e | 300mm wide PERFORATED type cable tray with support | Rmt | 30
6 | SITC OF SWITCHES, SOCKETS, INCLUSIVE OF FRONT MOUNTING PLATE & BACK BOXES WITH ALL ACCESSORIES
a | 6A Switch for Lighting control. | Nos | 6
b | 6A Power Switch & Socket set | Set | 35
c | 6/16A Power Switch & Socket set | Set | 18
d | 6A Socket | Nos | 18
g | 6/16A Power and Switch & Socket in weather proof enclosure | Nos | 12
i | Door bell / call bell | Nos | 1
7 | WIRING & CONDUITING
7.01 | SITC of concealed point wiring using 600V grade 3 x 2.5 sqmm FRLS copper conducter insulated wires with proper pulled through GI conduit clamped on over head slab, laid over false ceiling or in wall chases. Rate to include making good the wall chases with cement mortar, WITH JUNCTION BOX ALL REQUIRED ACCESSORIES. (of any wire length, NO EXTRA LENGTH WILL BE PAID)
a | Primary light points on switch BOARD (Without Switch & MCB cost- switch to be billed in section 8 above, CIRCUIT LENGTH OF SWITCH BOARD TO PANEL/DB TO BE BILLED IN RESPECTIVE SECTION) | Nos | 4
B | Primary light points on MCB control | Nos | 10
C | Secondary light points BY Switch or MCB | Nos | 21
7.02 | SITC of FRLS circuits pulled through GI conduits clamped on over head slab, laid over false ceiling or in wall chases. Rate to include making good the wall chases with cement mortar.
e | 2X6.0 + 1X4.0 sq.mm. CU FRLS wires, circuit from DB or panel to power point (Equipment) | Rmt | 40
f | 2X4.0 + 1X2.5 sq.mm. CU FRLS wires, circuit from DB or panel to power point (Equipment) | Rmt | 480
H | 2X2.5 + 1X1.5 sq.mm. CU FRLS wires, circuit from DB or panel to power point (Equipment) or switch board for lighting | Rmt | 850
8 | EARTHING
8.01 | SITC of earthing wire including necessary accessories, clamped on over head slab or walls, laid over false ceiling or in wall chases. Rate to include making good the wall chases with cement mortar. Interconnection between lengths should be as per specifications and as per good installation practice.
b | 25 X 3 mm GI Strip | Rmt | 100
d | 8 SWG hard drawn bare GI wire | Rmt | 200
e | 12 SWG hard drawn bare GI wire | Rmt | 150
8.02 | SITC of runs of insulated copper wire as earthing conducter including necessary accessories, clamped on over head slab or walls, laid over false ceiling or in wall chases. Rate to include making good the wall chases with cement mortar. Interconnection between lengths should be as per specifications and as per good installation practice.
b | 1C X 16 sq. mm. | Rmt | 60
8.03 | SITC of Copper Earthing station as per specification and IS: 3043-1985 for equipment earthing for UPS and IT earthing. Following guidelines to be maintained: | Nos
a | Excavation in hard marrum
b | Watering pipe
c | Earthing strip / Earthing cable
d | Plate / pipe electrode
e | Hardware
F | Brick masonry chamber with C.I. hinged cover and funnel
G | Charcoal and salt fill
H | Equipotential bar
I | 600 x 600 x 3 mm. Thick CU. Earth electrode type earth station
J | Brick masonry chamber with C.I. hinged cover and funnel | Nos
8.04 | SITC of GI Earthing station as per specification and IS: 3043-1985 for equipment earthing for panel and equipment earthing. Following guidelines to be maintained: | Nos
a | Excavation in hard marrum
b | Watering pipe
c | Earthing strip / Earthing cable
d | Plate / pipe
e | Hardware
F | Charcoal and salt fill
G | Equipotential bar
H | 600 x 600 x 6 mm. Thick GI Earth electrode type earth station
I | Brick masonry chamber with C.I. hinged cover and funnel
J |  | Nos
8.05 | SITC of Chemical Earthing station as per specification and IS: 3043-1985 for equipment earthing for panel and equipment earthing. Following guidelines to be maintained: | Nos | 0
a | Excavation in hard marrum
b | Chemical compound
c | Earthing strip / Earthing cable
d | Cu pipe in pipe electrode
e | Hardware
F | Equipotential bar
G | Brick masonry chamber with C.I. hinged cover and funnel | Nos | 0
8.07 | SITC of 25 x 4mm GI Earth Bus in powder coated box | Nos
9 | SIEMENS /L&T MAKE MK1 3 PHASE DOL STARTER FOR ALL EXHAUST FAN/FRESH AIR/INLINE FAN
9.01 | 5.5 KW | Nos
9.02 | 3.7 KW | Nos
9.03 | 2.2 KW | Nos
10 | TELEPHONE / DATA / TV
10.01 | SITC of RJ45 information outlet with face plate and box | Nos | 10
10.02 | SITC of RJ11 telephone outlet with plate and box | Nos | 3
10.03 | SITC of CAT6 data cable EXCLUDING 20mm/25mm dia. conduits | Rmt | 300
10.04 | SITC of CAT5 cable EXCLUDING 20mm/25mm dia. conduits for telephone | Rmt | 80
10.05 | SITC of 10 pair telephone tag block with enclosure | Nos | 1
11 | INSTALLATION OF LIGHTING FIXTURES
A | FIXING OF LIGHT | Nos | 31
18 | P/L OF PVC TRUNKING WITH CAP
A | 4" WIDE | RMT
B | 6" WIDE | RMT
1 | Supply & Installation
a | Supply of Main LT panels | 1 | Nos
b | Supply of 18 Way SPNDB | 1 | Nos
2 | UPS
2.01 | Supply,Installation,Testing & Commissioing of single/Three phase UPS with 20minute battery back-up online systems with 2 nos DP MCB in weather proof enclosures. 3KVA -single phase input and single phase output ups with 25A DP MCB and 25A DP MCB on input and output of ups. 6KVA - single phase input and single phase output ups with 40A DP MCB and 40A DP MCB on input and output of ups.
d | 6 KVA Floor Mounted | 1 | Nos