## GAS PIPING- BOQ
DATE
Budweiser -LUCKNOW AIRPORT
BOQ FOR GAS PIPING SYSTEM
S/NO | DESCRIPTION | Make | Qty. | UNIT | Unite price
[5 empty] | Supplay | Installation | Amount
1 | PNG Gas Daiphram Type Meter Model G-4 , Running Pressure 2-bar, Flow Rate 6 m3/h with fiting (elbo,tee,Cupler) | honywell/Matrix | 1 | Nos. | 20500 | 4715 | 25215
2 | Pressure Control Regulator RJ-4 Inlet 0 to 19 bar, Outlet 0 to 1.5 Bar | United/honywell | 1 | Nos. | 3200 | 736 | 3936
3 | Gas Filter 25mm almuniam Body | Vanaz/Honywell/Vel | 1 | Nos. | 3950 | 908.5 | 4858.5
4 | Pressure Gauge 4" Dail 2.5 Bar | Mahaveer/ H-guru | 2 | Nos. | 2850 | 655.5 | 7011
1 | MS Pipe 40 mm NB Sch. 40 , ASTM A 106 , ANSI B36.10 Including , MS Fitting (Elbow. Tee, Reducer ANSI B16.5 , 11 ) MS Support , U-Clamp , M clamp , Sleeve and ancher Fastner . | Tata/Jindal/MSL | 25 | RMT | 1050 | 241.5 | 32287.5
2 | CS Ball Valve 40 NB Flanged end 150 # single pc design ASME-B16.10 | L&T/Volson | 2 | No. | 5500 | 1265 | 13530
3 | CS Ball Valve 25 NBScrewed , NPTTF end, 3 pcs design ASME B16.10 (for Used Point) | L&T/Volson | 2 | Nos. | 4500 | 1035 | 11070
4 | Painting of pipes. 2 coats of red oxide and 2 coats of Golden Yellow final paint. Total 120 microns thickness | Acian/Burger | 25 | RMT | 95 | 21.85 | 2921.25
6 | Hose Pipe 3/4" , Dia ,2mtr Lent Havy Duty Black Used Point | Hyflex/suraksha | 2 | Nos. | 1650 | 379.5 | 4059
7 | Testing & commissioning of Pipe with Nitrogen gas for Testing with pressure of 6 Bar to test all joints with soap test for the leakage , then it will be time holded for 4 hrs then 6 hrs & finally 24 hrs to check wheather the leakage is there or not. After this we will release PNG Gas & will start the line Test Pressure 6 air & 4-Bar Nitrojen | Job | 1 | JOB | 8500 | 1955 | 10455
| LPG Leak Detector & Alarm System | [5 empty] | 0
8 | Gas Leakage Detector Display Type | Ambetronic/Crimcent | 3 | Nos | 12500 | 2875 | 46125
| UNIQUE SPECIFICATION: - | [5 empty] | 0
| a. Certified CIMFR, BIS, PESO Tested Enclosure. No third party Enclosure is used | [5 empty] | 0
| b. Individual Enclosure check & Pressurise Test done as per IEC 60079-1 | [5 empty] | 0
| c. Enclosure: Protection Class: IP-66 | [5 empty] | 0
| d. Non-Intrusive programming for Flameproof Model using Magnetic Wand. | [5 empty] | 0
| e. Password protected programming with changing facility. | [5 empty] | 0
| f. Reverse Polarity Protection | [5 empty] | 0
| g. Calibration can be performed locally without the need for hot work permits. | [5 empty] | 0
| h. Display: 4-Digit 8 mm (H) 7-Segment LED Display | [5 empty] | 0
| I. Optimised for detection of smallest Gas leaks | [5 empty] | 0
| j. Highly resistant to poisoning & etching. | [5 empty] | 0
| k. Display Indicate Status of Instrument | [5 empty] | 0
0
9 | Control alarm Panel 4 zone | Ambetronics/Crimscent | 1 | Nos | 14500 | 3335 | 17835
| GENERAL SPECIFICATION: - | [5 empty] | 0
| oprating Pressure 230 v Acc | [5 empty] | 0
| - Operating Temperature: 0 to +50 degree C | [5 empty] | 0
| - Enclosure: Protection Class: IP-54 | [5 empty] | 0
| - Enclosure: M.S. Metal Sheet, Siemens Grey colour Powder Coated housing | [5 empty] | 0
| - Display :128x64 Graphical Display with Backlight | [5 empty] | 0
| - Status :4 numbers LEDs (AL1, AL2, Fault, Communication) to indicate the status of Alarm generation of Connected Detector & | [5 empty] | 0
| Relay Module | [5 empty] | 0
| - Cable Entry: 05 x ¾” ET | [5 empty] | 0
| - Single Compression Gland | [5 empty] | 0
| - Supply Voltage: 90VAC to 270VAC, 50Hz. | [5 empty] | 0
| - Enclosure Dimension: 300mm (H) x 320mm (W) x 105mm(D) | [5 empty] | 0
| - Weight: Approx. 4.3 kg | [5 empty] | 0
| - Mounting: Wall / Stand Mounting | [5 empty] | 0
| - Along with Basic mounting accessories such as Rawl plug, Self- | [5 empty] | 0
| Thread Screw, Plain Washer Spring washer etc. are included | [5 empty] | 0
10 | Solenoid valve with Fittings(25MM) 24V DC | Uflow/Techno | 1 | Nos | 7500 | 1725 | 9225
| End Connection : Thread | [5 empty] | 0
| Size : 25mm | [5 empty] | 0
| Body Material : SS ASTM A351 Grade CF8 / CF8M | [5 empty] | 0
| Diaphragm : Nitrile (NBR) | [5 empty] | 0
| Media Temp : -30°C to 90°C | [5 empty] | 0
| Circumstance Temp : -10°C to 70°C | [5 empty] | 0
| Main Features : Internal Parts are in superior corrosion resistance steel, (Equivalent to SS316L) Suitable for Food Industries, Pharmaceuticals, Chemical application & Highly corrosive environmen | [5 empty] | 0
| Operating Voltage /Power Consumption : 24DC 11W | [5 empty] | 0
11 | Siren Flash / Hooter 24V DC | agni | 1 | Nos | 1250 | 287.5 | 1537.5
12 | Meter Box (size 20"x24") MS Framing , door almuniam haff net type | Fabricated | 1 | Nos | 6500 | 1000 | 7500
13 | Armoured cable 3C x 1.5mm | Pollycabe | 25 | mtr | 140 | 32.2 | 4305
| TOTAL | [5 empty] | 201870.75