## SUMMARY
BOQ SUMMARY |  | SUBWAY
| Location & Address | Subway T1 NAVI MUMBAI
| Format | AIRPORT | Date of Opening
| Total Area (Sq.Ft) | 628 | Vendor
| Landlord Investment |  | Site Incharge
S.No. | DESCRIPTION | AMOUNT | GST % | GST AMT | AMOUNT WITH TAX | PER Sq.Ft | REMARKS
1 | CIVIL & INTERIOR |  | 18%
2 | ELECTRICAL WORK |  | 18%
3 | HVAC HIGH SIDE |  | 28%
4 | HVAC LOW SIDE |  | 18%
5 | PLUMBING WORK |  | 18%
6 | FIRE FIGHTING WORK |  | 18%
8 | Additional Work |  | 18%
| TOTAL CIVIL & INTERIOR WORK | 0 |  | 0 | 0 | 0

## Electrical Work
BOQ OF ELECTRICAL WORK
SL.NO | DESCRIPTION | UNIT | QTY | Rate | AMOUNT | Remark
A | WIRING SYSTEM
NOTE:- 1. Only FRLS conductor wire shall be used; 2. Conduit carrying circuit wiring should not carry point wiring and Conduit (GI/PVC) carrying point wiring should not carry submain/circuit wiring; 3. The wires from ceiling junction to light points / light fixture shall be drawn in flexible PVC/GI conduit with adptor & cover for junction box & crimp type lugsat both the ends along with necessary hardware & accessories, etc. as required; 4. Proper ferrules, lugs, must be used in all cabling and wiring on both load / source end; 5. Each switch board must be provided with respective ferrules representing the respective DB, Phase & Circuit numbers; 6. Looping of Neutral / Earth wire between two seperate Primary / Full Points is strictly not allowed; 7. Looping of Neutral /Earth wire between two seperate circuits on similar or other phase is strictly not allowed; 8. Ferulling / numbering / taggning to wires with circuit number & db name for all lighting & raw / ups power shall be strictly followed at both DB & switch board / switch socket boards ends. 9. Point wiring in open area or heating area like kitchen /under false ceiling will be done using GI conduit. conceald wiring will be done using PVC conduits.
1 | Provide all materials, accessories, labour etc. for wiring for lights, using 2runs 2.5 sqmm PVC insulated stranded copper conductor FRLS wires of 1100/670V grade drawing through Medium gauge rigid MS conduit of 25mm dia with 1.6mm (HMS) wall thickness including supply and laying of conduits and its accessories above false ceiling using PVC pull/junction boxes, light outlet boxes including testing and commissioning complete. Db to switch board will be paid in submain wiring and from switch borad to first light point,db to first light & db to switch will consider as primary light point and lopping will consider as secondary light point.
LIGHTING CIRCUIT PRIMARY
Note: All the lighting points will have 6A PVC connector at the end of the point for connection in lights
1.1 | Primary light point controlled with 3 Runs 2.5sqmm Cu FRLS flexible wires in 25mm PVC/GI HMS Conduit, from DB to switch | Nos | 11
1.1.a | UPS primary point
| For UPS |  | 3
1.1.b | Raw primary point
| Outside light |  | 2
| Dining area |  | 1
| Service Area |  | 2
| Bathroom |  | 1
| Boh |  | 1
| Storage |  | 1
11
1.2 | Primary light point controlled with 3 Runs 2.5sqmm Cu FRLS flexible wires in 25mm PVC/GI HMS Conduit, from switch to switch
1.3 | Primary light point controlled with 3 Runs 2.5sqmm Cu FRLS flexible wires in 25mm PVC/GI HMS Conduit, from switch to light / light to switch
1.4 | Primary light point controlled with 3 Runs 2.5sqmm Cu FRLS flexible wires in 25mm PVC/GI HMS Conduit, from DB to light
LIGHTING CIRCUIT SECONDRY
1.5 | Secondary light point with 3 Runs 1.5sqmm Cu FRLS flexible wires in 25mm PVC/GI MMS Conduit from light point to light point | Nos | 14
1.5.a | UPS Secondary point
| Service Area |  | 1
| Entry outside |  | 1
| Boh |  | 1
1.5.b | Raw Secondary point
| Service Area |  | 2
| Dining Area |  | 2
| Outside |  | 4
| Bathroom |  | 1
| Storage |  | 1
| Boh |  | 1
14
2 | POWER CIRCUIT MAIN
Providing all materials, accessories and labour for wiring for PVC conduit and accessories for wiring 6A sockets, 6/16A sockets, 16/20A sockets single phase and 25A, 3 phase commercial / industrial type sockets using PVC insulated stranded copper conductor wires of 650V grade drawn through Medium gauge rigid MS conduit using necessary conduit accessories, PVC pull/junction boxes, G.I. fish wire etc. The wiring cost shall include cost of wires, conduit and its accessories and earth wire. (The G.I. outlet box and the socket measured separate).
2.1 | 1C,3NO.X4 sqmm CU Flexible wire in existing medium guage pvc conduit / GI Conduit DB to power outlet ( For Raw Power Points, in kitchen/spare, refer SLD.) | RMT | 130
2.1.1 | DB to AC Unit Indoor |  | 8
2.1.2 | DB to Geyser |  | 12
2.1.3 | Db to UPS IN and Out |  | 26
2.1.4 | DB to Micro wave oven |  | 9
2.1.5 | DB to Makeline Machine 1 |  | 15
2.1.6 | DB to Makeline Machine 2 |  | 15
2.1.7 | DB to AC Outdoor 1 |  | 15
2.1.8 | DB to AC Outdoor 2 |  | 17
2.1.9 | Db to Griller |  | 13
130
2.2 | 1C, 3NO.X4 sqmm CU Flexible wire in existing medium guage pvc conduit / GI Conduit power outlet to power outlet ( For Raw Power Points, in kitchen/spare, refer SLD.) | RMT
2.3 | 1C,3NO.X2.5 sqmm CU Flexible wire in existing medium guage pvc conduit / GI Conduit DB to power outlet ( For Raw Power Points, in kitchen/spare, refer SLD.) | RMT | 481
2.3.1 | DB to 2 D Chiller |  | 9
2.3.2 | DB to 4 D Chiller |  | 8
2.3.3 | DB to 4 D Chiller |  | 7
2.3.4 | DB to Visi Cooler |  | 17
2.3.5 | Fly Catcher and Air Curtain |  | 19
2.3.6 | Db to Outside Front Light |  | 23
2.3.7 | DB to Signage |  | 26
2.3.8 | DB to Charging Point 1 |  | 17
2.3.9 | DB to Charging Point 2 |  | 19
2.3.10 | DB to Charging Point 3 |  | 24
2.3.11 | DB to Sphare Point outside railing light |  | 32
2.3.12 | DB to Bathroom |  | 25
2.3.13 | DB toTable Raw Power |  | 16
2.3.14 | UPS to Table Power |  | 15
2.3.15 | UPS to Fire Panel |  | 14
2.3.16 | USP To Manager PC |  | 15
2.3.17 | UPS DB to IT Rack |  | 14
2.3.18 | UPS To DMB |  | 13
2.3.19 | DB to 2 Pressure Pump |  | 15
2.3.20 | DB to Coffee Machine |  | 18
2.3.21 | Db to Lolipop |  | 41
2.3.22 | Db to spare |  | 20
2.3.23 | Db to store room |  | 25
2.3.24 | Db to Ro |  | 16
2.3.25 | Db to Servo |  | 15
2.3.26 | Db to S Logo |  | 18
481
2.4 | 1C, 3no.X2.5 sqmm CU Flexible wire in existing medium guage pvc conduit / GI Raceway power outlet to power outlet ( For Raw Power Points, in kitchen/spare, refer SLD.) | RMT
2.5 | 1C,4NO.X4 sqmm CU Flexible wire in existing medium guage pvc conduit / GI Conduit DB to power outlet ( For Raw Power Points, in kitchen/spare, refer SLD.) | RMT
2.6 | 12 ' Exhaust fan Supply and installtion | Nos.
3 | POWER RECEPTACLES.
3.1 | Supply and installation of 1 no. 6A shuttered switched socket outlet with 3M G.I.back box 3M cover plate Raw/ups supply | Nos. | 6
a | Charging Point |  | 3
b | Visi Cooler |  | 1
c | Led Stand Light |  | 1
| Air Curtain |  | 1
6
3.2 | Supply and installation of 2no. 6A shuttered switched socket outlet with 6M G.I.back box 6M cover plate Raw/ups supply | Nos. | 8
a | DMB |  | 3
b | Pos |  | 1
| Storeroom |  | 1
| Spare |  | 1
| CCTV Rack |  | 1
| Bathroom |  | 1
8
3.3 | Supply and installation of 3 no. 6A shuttered switched socket outlet with 8M G.I.back box 8M cover plate Raw/ups supply | Nos. | 1
3.4 | Supply and installation of 1 no. 16A shuttered switched socket outlet with 3M G.I.back box 3M cover plate | Nos. | 9
a | Pressure pump |  | 1
b | 2 D Frezeer |  | 1
c | Geyser |  | 1
| 4 D Frezeer |  | 2
| AC |  | 1
| Fire point |  | 1
| Ice machine |  | 1
| Griller |  | 1
9
3.5 | Supply and installation of 1 no. 20A shuttered switched socket outlet with 3M G.I.back box 3M cover plate | Nos.
3.6 | Supply and installation of 2 no. 6/16A shuttered switched socket outlet with 6M G.I.back box 6M cover plate | Nos. | 10
3.6.1 | UPS Input Output |  | 1
3.6.2 | Manager PC |  | 1
3.6.3 | Coffee Machine |  | 1
3.6.4 | Make Line 1 |  | 1
3.6.5 | Make Line 2 |  | 1
3.6.6 | Spare Point |  | 2
3.6.7 | Table UPS |  | 1
3.6.8 | Fly cather |  | 1
3.6.9 | Ro |  | 1
10
3.7 | Supply and installation of 1 no. 20A MCB oprated industrial socket outlet with G.I. enclosure | Nos.
3.8 | Supply and installation of 1 no. 25A MCB oprated socket outlet with G.I. enclosure | Nos. | 1
3.9 | Supply and installation of 1 no. 25A 3 phaseMCB oprated socket outlet with G.I. enclosure | Nos. | 2 |  |  |  | Use 32A 3 Phase MCB
a | Bread Baking Oven |  | 1
b | Speed Oven |  | 1
4 | JUNCTION BOR (POWER RECEPTICLE) | Nos.
4.1 | 3M backbox & 3M face plate | Nos. | 1
4.2 | 6M backbox & 6M face plate | Nos. | 3
4.3 | 6A switch | Nos.
4 | ISOLATORS / BREAKERS
4.1 | Supply and installation of 63 A TPN MCB,16 kA in IP55 Metal boards enclosure | No's
4.2 | Supply and installation of 40 A TPN MCB,16 kA in IP55 Metal boards enclosure | No's
4.3 | Supply and installation of 40 A TPN MCB,16 kA in IP55 Metal boards enclosure (For ODU) | No's
4.4 | 100A FP, 25kA Microprocessor based MCCB with LSIG Protection with weather proof Box, Near Mtr | No's
4.5 | 63A FP, 25kA Microprocessor based MCCB with LSIG Protection with weather proof Box, Near Mtr | No's
4.6 | 125A 4pole Change over Switch Manual type | No's
4.7 | 160A 4pole Change over Switch Manual type | No's
4.8 | 3 Phase Bus Bar Box Suitable for distribution of service connection from the single mains Multiple Outgoing From single Incoming Supply Suitable for outdoor | No's
5 | Supply, Installation , testing and commissioning of 3 KVA UPS 1-phase input & 1-phase output UPS inbuilt isolation tranformer. Quoted rate shall be inclusive of required batteries of 30 minutes back up at full load , connecting cables, Battery rack and and its accessories complete | No's
B | MV CABLES
1 | Supply & Installation of 1100V grade armoured cable having sector / circular shaped aluminium / copper conductor PVC insulated cores, laid up, PVC tape wrapped inner sheathed, GI strip / wire armoured and overall extruded PVC sheathed confirming to IS: 1554, laid on wall / ceiling using GI clamps & spacers as per route shown at site and further as directed by Consultant at site in the following sizes :- (Make - Polycab / Finolex / CCI / RR / Havells)
NOTE :- All Armoured cables shall be provided with temporary labelling at every 5mtrs & then finally with metal indentification tags showing the size & the location from/to the respective Panel / DB, at both the ends
1.1 | 3.5CX50 sqmm AL ARM cable clamped directly or layed through tray | RM
1.2 | 3.5CX35 sqmm AL ARM cable clamped directly or layed through tray | RM
1.2 | 4CX25 sqmm CU ARM cable clamped directly or layed through tray | RM
1.2 | 4CX16 sqmm CU ARM cable clamped directly or layed through tray | RM | 17
| DG TO DB |  | 17
1.2 | 4CX10 sqmm CU ARM cable clamped directly or layed through tray | RM
1.2 | 4CX6 sqmm CU ARM cable clamped directly or layed through tray | RM | 18
a | Speed Oven to DB |  | 8
b | Baking Oven to Db |  | 10
18
1.3 | 4CX4 sqmm CU ARM cable clamped directly or layed through tray | RM
1.4 | 3CX4 sqmm CU Flexible cable clamped directly or layed through tray | RM
1.5 | 5CX4 sqmm CU Flexible cable clamped directly or layed through tray | RM
1.6 | 3CX2.5 sqmm CU ARM cable clamped directly or layed through tray (AHU to DB) | RM
1.7 | 3CX2.5 sqmm CU Flexible cable clamped directly or layed through tray | RM
1.8 | 5C X 4 sq. mm. cable for oven installtion | RM
2 | GLANDING & TERMINATION :- Supply & Installation of end termination of above mentioned cables including compressed type brass glands, crimping type copper lugs, insulation tape etc. as 'required complete with earthing of glands in following sizes :-
2.1 | 3.5CX50 sqmm AL ARM cable clamped directly or layed through tray | Nos
2.2 | 3.5CX35 sqmm AL ARM cable clamped directly or layed through tray | Nos | 1
2.3 | 4CX25 sqmm CU ARM cable clamped directly or layed through tray | Nos
2.4 | 4CX16 sqmm CU ARM cable clamped directly or layed through tray | Nos
2.5 | 4CX10 sqmm CU ARM cable clamped directly or layed through tray | Nos | 1
2.6 | 4CX6 sqmm CU ARM cable clamped directly or layed through tray | Nos | 2
2.7 | 4CX4 sqmm CU ARM cable clamped directly or layed through tray | Nos
2.8 | 3CX4 sqmm CU Flexible cable clamped directly or layed through tray | Nos
2.9 | 5CX4 sqmm CU Flexible cable clamped directly or layed through tray | Nos
3 | 3CX2.5 sqmm CU ARM cable clamped directly or layed through tray | Nos
C | LIGHT FIXTURES
Supply & Installation, testing and commissioning of following type of light fixtures as per drawings and specifications with all other accessories such as supporting rods / frames, anchor fasteners, necessary hardware etc. The rate shall include for installing the fittings along with transformers where required, lamps, diffuser, chokes, starter, power factor improvement capacitors, wires, downrods etc., complete with all accessories to complete the installation as required. All Electronic ballast shall be with harmonic distortion less than 10 thd. all the lights should be dimming and autamation supportive and light which is going to be used in liquor storage should be fire proof. rate including clutch ware up to 3mtr) ( Kindly Refer the Lighting Layout and the Details provided by Architect for all light fixtures. )
NOTE : PLEASE REFER LIGHTING LAYOUT LEGEND FOR LIGHT FIXTURE DETAILS
1 | INDDOR LIGHT
1.1 | 115mm RECESSED DOWNLIGHT | Nos.
1.2 | SUSPENDED LINEAR CHANNEL LIGHT | Nos.
1.3 | 595X595 MM RECESSED LED LIGHT,tube light | Nos.
1.4 | SITC OF SINAGE LIGHT 3W | Nos.
1.5 | 12-18W -Recessed Down light (False ceiling light) | No's
1.6 | LED Spot Lights - 5watts | No's
1.7 | 40w OPTIMUS T5 Tube light LED (48") | No's
1.8 | 2'x2 Led Panel Light with hanging/Ceiling fitting arrangement | No's | 16
1.9 | 1'x4' Led Panel Light with hanging arrangements (includes Clutch wires) | No's
1.11 | 1 Meter Track White (includes Clutch wires) | No's | 1 |  |  | Track Light 3 Nos.
1.12 | 2 Meter Track White | No's
1.13 | 10 W White Track light to be monted on above mentioned tracks | No's
1.14 | Linear Light 8 Feet, 4feet | Rft | 12
1.15 | 1200mm Wide Ceiling Fan | No's
1.16 | 9" Exhaust fans in PVC body and blade with folding louvers | No's
1.17 | 12" Exhaust fans in PVC body and blade with folding louvers | No's
1.18 | 9" Exhaust fans Hevy duty industarial Fan Make (almonard) | No's
1.19 | 12" Exhaust fans Hevy duty industarial Fan Make (almonard) | No's
1.2 | 18" Exhaust fans Hevy duty industarial Fan Make (almonard) | No's
1.21 | 24" Exhaust fans Hevy duty industarial Fan Make (almonard) | No's
1.22 | Door bell / call bell | No's
1.23 | SUSPENDED LINEAR CHANNEL LIGHT (only fixing) | nos | 2
D | MEDIUM VOLTAGE PANELS & DISTRIBUTION BOARD
1 | SMALL DISTRIBUTION BOARDS
Design, supply, installation, testing and commissioning of following miniature type circuit breaker type boards, wall mounted (flush / surface) as per drawings and specifications and as required. The distribution board shall be of sheet steel enclosure with copper busbars suitable for single phase or three phase MCBs. The MCBDB shall have sheet steel hinged lockable door top to prevent access to MCBs from outside. The DB shall have suitable neutral and earth terminal block to facilitate easy termination of wires. All wires inside the DBs shall be terminated using copper end terminations.
1.1 | FABRICATED DB (refer SLD) (Having fire separation system)
| Supply, Installation, Testing & Commissioning of 6way PPI IP -43 DB, incomer-63A 4pol MCB-1. outgoing-40A RCCB-3 No..10/16A SP MCB-30(Lighting & Kitchen Power DB) | Nos
1.2 | LIGHTING & POWER DISTRIBUTION BOARD -( 8-WAY SPN DB )
LPDB - Comprises
Incomer having:
One nos(1) - 32A, 4pole, 16kA, RCCB, C-CURVE
Outgoing feeders:
Four nos (3) 20A, SP,10 ka, MCB, C-CURVE
four nos (1) 16A, SP,10 ka, MCB, C-CURVE
| LPDB as above | Nos
1.3 | UPS POWER DISTRIBUTION BOARD -( 8-WAY SPN DB )
UPSDB - Comprises
Incomer having:
One nos (1) - 32A, DP, 100mA, RCCB, C-CURVE
Outgoing feeders:
Six nos (6)- 16A, SP,10 ka, MCB, C-CURVE
| UPSDB as above | Nos | 1
1.4 | 12WAY- TPN DB WITH IP 42- #IK 09 WITH METAL DOOR | Nos
1 no- 100A 4P MCCB -1no.
3 nos- 32 amps DP 30mA RCBO(outgoing)
24 nos- 10/16/25 amps SP MCB
1.5 | 6WAY- SPN DB WITH IP 42- #IK 09 WITH METAL DOOR | nos
Incomer : 25A DP ELCB, 100mA - 1no.
Outgoings : 6 Nos,10A SP MCBs
1.6 | 8 way VTPN ( MCCB Incoming of 250A frame) | nos
8 Way VTPN MCB DB with Metal Double Door protection IP 42
Incomer : 250A TPN MCCB ISOLATOR-1no.
Outgoings : 8 Nos 32A TPN MCB's
Outgoings : 2 Nos 40A TPN MCB's
Outgoings : 2 Nos 63A TPN MCB's
1.7 | 8 way 7 Segment DB metal door type | Nos | 1
DB01:
1 no- 100 amps 4P MCB(Incoming)"C" Curve
3 nos- 32 amps DP 30mA RCBO(outgoing)
24 nos- 10/16/25 amps SP MCB(outgoing)"C" Curve
Make:SCHNEIDER/SIEMENS/LEGRAND/HAGER
E | DATA NETWORKING, VOICE,TV,RACEWAYS ( Network Cable Make : Preferred Systemax )
1 | Providing and laying of medium gauge rigid PVC conduit with all conduit accessories PVC junction/pull boxes, G.I fish wire, fixing accessories etc as required for telephone and data networking complete. The rates shall include chasing of walls, floors etc & plastering the chased portion as required.
1.1 | 25mm dia MS FRLS Conduit ( FA,PA,Data, voice, power etc.) | Mtrs
1.2 | 32mm dia MS FRLS for HDMI if required | Mtrs
1.3 | 25mm dia PVC FRLS Conduit ( FA,PA,Data, voice, power etc.) | Mtrs | 30
1.4 | 32mm dia PVC FRLS Conduit | Mtrs
2 | Supply & installations of MS Powder Coated, 2.0mm Thick, 50mm height, readymade Perforated Type cable trays (With/without Removable Top Cover) complete with couplers, bends etc. The rate to include supports of 25x25mmx3mm of angle with 10mm verticle rods fixed with 6mm Anchor fasteners. The vertical support shall be placed at interval of not more than 1.5 Metrs & at all bends. All offsets bends shall be factory fabricated. Color Shade of powder coating shall be as per Architect's Choice. (For Power & Networking Cabes)
2.1 | 300mm wide | Mtrs | 25
2.2 | 150mm wide | Mtrs
2.3 | 100mm wide | Mtrs
2.4 | G.I TRUNKING WITH COVER 1.6 MM thichnes
2.5 | GI Trunking With cover=150mm x40mm x1.6mm | Mtrs
2.6 | GI Trunking With cover=100mm x40mm x1.6mm | Mtrs
2.7 | PVC wire maneger =100mm wide x50mm height.for server rack | Mtrs
3 | RACEWAYS
SITC of al raceways 1.6 mm thick and junction boxes of GI having 2mm wall and 2.5mm thick conver plate with all necessary accessories including the cost of floor cutting.
3.1 | 100 x 40 mm | Mtrs
3.2 | 200 x 40 mm | Mtrs
3.3 | 150 x 150 x 50 mm jb with hing type stainless steel cover | No
3.4 | 200 x 200 x 50 mm jb with hing type stainless steel cover | No
4 | Supply and wiring for Data and telephone with enhanced CAT-6e, 4pair cable in existing conduit/ raceways with end terminations. | Mtrs | 165
a | BM to It Rack
b | Data 1 |  | 12
c | Data 2 |  | 12
d | Data 3 |  | 13
e | Data 4 |  | 13
f | Data 5 |  | 14
g | Data 6 |  | 15
Counter Area
h | Data 1 |  | 8
i | Data 2 |  | 8
| Data 3 |  | 9
Manager PC
J | Data 1 |  | 5
K | Data 2 |  | 6
L | CCTV 1 |  | 9
M | CCTV 2 |  | 8
N | CCTV 3 |  | 10
O | CCTV 4 |  | 12
P | CCTV 5 |  | 11
165
5 | Supply, installation, testing and commissioning of clip on type Data Outlets mounted on a GI outlet box with front plate and all necessary accessories complete as required including the termination of wires. (RJ45) | No
6 | Supply, installation, testing and commissioning of plug on type Telephone Outlet mounted on a GI outlet box for cat 6 with front plate and all necessary accessories complete as reqd including the termination of wires.(RJ11) | No
7 | HDMI Cable (5mtr) with moulded end connectors + 40 mm PVC Conduit with Accessories | No
8 | Supply & installation of Telephone junction box with 20-pair Krone | No
9 | 50Pair armoured Jelly filled 0.5sqmm annealed copper telephone cable with necessary supports | Mtrs
10 | Supply, installation, testing and commissioning of 5U Rack with all necessary accessories complete as reqd (WITH POE SWITCH ETC. ACCESSORIES) | No
11 | Supply, installation, testing and commissioning of 24U Patch Panel with all necessary accessories complete as reqd | No
12 | WIFI Routers 10meter range | No
F | EARTHING SYSTEM
1 | Providing and laying earthing conductors of copper strip/wire including necessary accessories, clamping to walls, cables etc. as required and interconnection between lengths as per specifications and as per good installation practice. The rate shall include all supports, accessories and hardware necessary for proper installation. |  | 1
Excavation in hard marrum
Watering pipe
Earthing strip / Earthing cable
Plate / pipe electrode
Hardware
Brick masonry chamber with C.I. hinged cover and funnel
Charcoal and salt fill
Equipotential bar
600 x 600 x 3 mm. Thick CU. Earth electrode type earth station
1.1 | 25 x 4mm Cu STRIP | Mtrs
1.2 | 1C, 16SQ.MM CU CABLE | Rm
1.3 | 1C, 10SQ.MM CU CABLE | Rm
1.4 | 1C, 6SQ.MM CU CABLE | Rm | 15
G | FIRE ALARM SYSTEM
1 | Supply, installation, testing and commissioning of 2Zone fire alarm panel with battery backup for operation, with battery charger. | No. | 1
2 | SITC of Smoke Detector with Standard base, Junction box and other accessories | Nos | 3 |  |  |  |  | smoke quanity
3 | SITC of Smoke Detector (above false ceiling ) with Standard base, Junction box and other accessories | Nos | 0
4 | SITC Response indicator for proposed detectors, compatible with any detector make. | Nos | 0
5 | SITC Supply Installation of Electronic Hooter cum Strobe. | Nos | 1
6 | SITC Supply Installation Manual call point. | Nos | 1
7 | Heat detectors | Nos | 1
8 | Supplying, installing, testing and commissioning approved make 2 core 1.5 sq. mm armoured PVC insulated copper Cable. | Mtrs | 200
9 | Control Module for Integration of Fire System with other security system | nos | 1
I | CCTV SYSTEM - ANALOGUE CAMERA'S (BOSH)
1 | SITC of 16ch NVR, H.264, 200 (PAL)ips recording rate, Up to 8ch audio inputs and 1ch audio outputs, Max 4 internal HDD (HDD x 4), DVD-RW, Built-in web viewer with IP Connectivity for Remote Access of the System via internet. 2TB harddisk. ( The DVR shall Record/Start Recording with Motion Control ) | No. | 1
2 | Supply and wiring for CCTV system using CAT-6 FR Copper Cable in existing conduit | Rm | 100
3 | Supply and wiring for CCTV system using 4+1 Copper Cable in existing conduit | Rm | 110
4 | Supplying and laying of Medium gauge rigid PVC conduit with all conduit accessories PVC junction/pull boxes, G.I fish wire, fixing accessories etc as required for Access Control Cables. The rates shall include chasing of floors etc & plastering the chased portion as required.
4.1 | 25mm dia MS FRLS Conduit ( FA,PA,Data, voice, power etc.) | Mtrs | 70
4.2 | 32mm dia MS FRLS for HDMI if required | Mtrs
4.3 | 25mm dia PVC FRLS Conduit ( FA,PA,Data, voice, power etc.) | Mtrs
4.4 | 32mm dia PVC FRLS Conduit | Mtrs
J | MISCELLENOUS
1 | Supply & Installation of 1.1KV Grade Rubber Mats. | Sqm
2 | Supply & Installation of Danger Notice Board etc | Job
3 | Supply & Installation of Charts/drawings/Single Line Diagram duly framed with front glass. | Job | 0
4 | Temporary Power & Lighting distribution phase wise for each lab for all agencies to work including suitable protection through MCBs/ELCBs/MCCBs & wiring & cabling. Construction power distribution tap off will be provided at the floor level along with the socket DB & from that point onward distribution to be considered in elect vendor's scope of work. The Temporary Lighting shall have an average of 150 to 200 Lux at all places maintained. Temporary Power required is approx 10 Kw per floor, which shall be coordinated with Developer for required Tap-off arrangement at each floor. | Job | 0
The rate shall include statutary aproval from Local Electrical Inspectorate & other required satatutary bodies, Preparation of AS-BUILT drawings, Testing of the installation & preparaition of test report as required by statutary bodies.
5 | TAGGING of Cables and circuits | Job | 0
6 | Music system with amplifere stand | no | 0
7 | Speakers | nos | 0
9 | light fixture assembly hardware fittings | Nos
TOTAL OF ELECTRICAL WORK

## Make list
NMIAL MAKE LIST
Package | Material Description | Model Number | Make
FAS
1 | Smoke Detector | TC806B3010 | Honeywell
2 | Multi sensor | TC806B3004 | Honeywell
3 | Heat detector | TC8B3102 | Honeywell
4 | Control module (For Hooter cum storbe ) | TC810N1013 | Honeywell
5 | Monitor module | TC809A1059 | Honeywell
6 | Mini Monitor module | TC809B1008 | Honeywell
7 | Relay Module | TC810R1024 | Honeywell
8 | Manual call stations | S464G1007 | Honeywell
9 | Hooter cum Strobe | SYS-ST | Honeywell (System sensor)
10 | Fire Resistant FRLS/LSZH Cables up to 1100V grade |  | Polycab,RPG Cable,Kunth Cab,Orbit,KEI,Ravin Cables,Finolex.
11 | Response Indicators |  | Honeywell or Reputed make
12 | Double compression cable gland |  | Baliga Lighting ltd,Comet,Dowells,Braco,cosmos
13 | Cable Lugs |  | comet,Dowells,cooper alloy ltd),Braco,Cosmos
14 | GI Conduit |  | Vimco,BEC,AKG
Fire Fighting
1 | GI Pipes (IS:1239 and IS:3589) |  | Tata Steel ,Jindal (Hissar)
2 | Grooved Joints above 50mm |  | Victaulic,Grinell,Recomb,Interfit,Jinan
3 | Standard MS fittings below 50mm |  | Industrial Valves and company
4 | Forged steel fittings below 50mm |  | VS Enginnering , JK Forging
5 | Fastner |  | Hilti ,Fisher
6 | Welding rods |  | Advani,comos,Prima,superbond,Ador
7 | Sprinklers /Nozzles(ULListed ,FM Approved) |  | Tyco,Grinell,HD,Viking,Globe,Reliable
8 | Flexible Sprinkler drops SS Braided |  | EsyFlex,Tyco ,Viking,Victaulic(Aquaflex),Newage Flex
9 | Butterfly valve (PN 16) |  | Audco,,KSB,Danfoss,Advance,Victaulic,NIBCO
10 | Wafer Type Check Valve |  | Advance ,Kirloskar ,Audco
11 | Pressure Reducing Valve |  | Leader zoloto RB
12 | Air Release Valve |  | Zoloto,RB,ITAP,TBS
13 | Clean agent Fire Supression system |  | Sapphire,kidde,NITIE 1230(for pressure 25 Bar )MX1230.
14 | Paints |  | Asian Paints,Shalimarpaints,Berger Paints
15 | Flow Switch |  | Tyco,Grinell,Kennedy,Shield(UK),Potter
16 | Fire Extinghusher |  | Alert Tyco,Minimax,Safex
17 | Pipe Protection Pypcoat (AW4)Wrapping |  | IWL or equivalent
18 | Presshure Gauge |  | H Guru, Fiebig, Dwyer
Plumbing
1 | a. Vitreous China Sanitaryware |  | Parryware, TOTO, Kohler, American Standard, Cera
2 | b. WC Connectors |  | Multikwik (UK), Jaguar
3 | Rain Water Outlets |  | Neer, GMGR
4 | Seat Cover (Heavy Duty) |  | Commander, Jaguar
5 | Bath Tub and Shower Tray |  | Woven Gold, Eurospa, Aquaplus, Jaguar
6 | Stainless Steel Sink |  | Prestige, Kingston, Neelkanth, Jaguar
7 | Auto Urinal Flush System |  | AOS Auto Robo Flushing System, Toshi, UTEC System, Askon Engineers
8 | Hand Drier |  | Kopal, Blue Circle, UTEC System, Askon Engineers, Philips, Bobrick
9 | CP Brass Fittings |  | Jaguar, Gem, Ess - Ess, Aquaplus, Viega
10 | Angle valve with filter |  | Arco
11 | Floor Drain Fixture, Rain Water Outlets & Channel Gratings |  | Neer, GMGR, Aco, Geberit, Viega
12 | C.P. Grating for Floor Trap |  | Chilly, GMGR, Neer, Viega
Cast Iron Pipes & Fittings & CI/DI Manhole covers and frames
13 | a. In accordance with IS:3989 (Pipes & Fittings) |  | NECO, Kapilansh
15 | b. In accordance with IS:1729 (Manhole covers and frames |  | NECO, Raj Iron Foundry -Agra, BIC - Calcutta, Kajeco, Crescent
16 | c. In accordance with IS:1536 |  | Kesoram - Calcutta, Electrosteel- Calcutta, IISCO
17 | CI Hubless Pipes |  | NECO, Kapilansh
18 | Ductile Iron pipes |  | Electrosteel, Jindal, Lanco
19 | Ductile Iron pipe fittings |  | Electrosteel, Kejariwal, Kiswock
20 | GI Pipes (IS: 1239 and IS: 3589) |  | Tata Steel, Jindal (Hissar), Zenith
21 | GI pipes fittings |  | Unik, Zoloto M, R Brand, Kirti
22 | Copper Pipes & Fitting |  | Rajco, IMI - Yorkshire, GMGR, IBP - UK, Viega
23 | PVC Pipe |  | Supreme, Ajay, Finolex
24 | Polypropylene Pipes |  | Dizayn, Prince, Kissan
25 | CPVC pipes |  | Astral, Prince, Kissan
26 | Polybutlene pipes |  | George Fisher or Equivalent
27 | RCC Pipe |  | KK, Pranali, Premier
28 | HDPE Pipes |  | Jain, Reliance, Prince, Kisan
29 | Stoneware Pipes, Gully Traps |  | Perfect Potteries-JABALPUR, Equivalent ISI marked
30 | SS Pipes |  | REMI, Viega, V.S. Metal
31 | GM / Forged Brass Valves |  | Leader, Zoloto, RB, Arco, GS, Danfoss
32 | Sluice Valves |  | Kirloskar, Indian Valve Company, H. sarkar
33 | Butterfly Valve |  | Audco, KSB, Danfoss, Advance, Victaulic, NIBCO
34 | Wafer Type Check Valve |  | Advance, Kirloskar, Audco
35 | Pressure Reducing Valve |  | Leader, Zoloto, RB
36 | Solenoid Valve |  | Avcon, Danfoss
37 | Steam Pressure Reducing Station / Valve |  | JN Marshall, Zoloto
38 | Steam Control / Isolation Ball / Gate / Globe Valve |  | Leader, Zoloto, RB, Kitz
39 | Plug Valve |  | Audco or Equivalent
40 | Air Release Valve |  | Zoloto, RB, ITAP, TBS
41 | Y Strainer |  | Emerald, Zoloto, Advance, Crane
42 | Hydropneumatic System |  | DP, Grundfos, ITT Industries
43 | Storm Water Drainage Sump Pumps |  | DP, Grundfos, ITT Industries, KSB
44 | Sewage Handling Pumps |  | DP, Grundfos, ITT Industries, KSB
45 | Dewatering Pump |  | DP, Grundfos, ITT Industries, KSB
46 | Drinking Water Cooler |  | Usha, Blue Star, Voltas
47 | Hot Water Pumps |  | DP, Grundfos
48 | Borewell Pump |  | DP, KSB
49 | Rotary Gear Pump |  | PEC, Rotodel
50 | Motor |  | Siemens, Bharat Bijlee, ABB, Kirloskar
51 | Mechanical Seal |  | Burgmann or Equivalent
52 | Couplings |  | Lovejoy or Equivalent
53 | Anti Vibration Mounting |  | Kanwal Industrial Corporation, Dunlop, Resistoflex, Corporation
54 | Pressure Gauge |  | H Guru, Fiebig, Dwyer
55 | Water Meter (Mechanical Type) |  | Kaycee, Dashmesh, Sant
56 | Electronic Flow Meter
57 | Level Controller (Water) |  | Technika, Minilec, Danfoss
58 | Level Indicator (Water) |  | Technika, Minilec, Danfoss
59 | Level Indicator (Oil) |  | Forbes Marshall or Equivalent
60 | Paints |  | Asian Paints, Shalimar Paints, Berger Paints
61 | MH / Water Tank Plastic Steps |  | KGM, Patel, Pranli Industries
62 | Water Treatment Plant |  | Thermax, Ion Exchange, Watcon, EA Water
63 | Water Treatment Vessel |  | Astral, Structural
64 | Ultra Violet Water Purifier |  | Eureka Forbes, Trojan, Kent, Aquatech, Eurostar
65 | Dosing Pumps |  | LMI, Toschon, Pulser Feeder
66 | Garbage Crusher |  | Venus or Equivalent
67 | Water Supply Nozzle |  | Astral or Equivalent
68 | Insulation for Chimney & Steam Pipes |  | Lloyd Insulation, UP Twiga
69 | Insulation for Hot Water Pipes |  | Armacell - Armaflex (UK / German), Eurobatex – Union Foam (Italy), Trocellen
70 | Electric Water Heater |  | Venus, Bajaj, Spherehot, Idotripi
71 | Insulation for Steam Pipes |  | Lloyd Insulation or Equivalent
HVAC
1 | Air Handling Unit |  | Flaktwoods/Carrier/Trane/ ETA/Voltas/Zeco/Caryaire/Saiver/VTS
2 | Fan Coil Unit |  | Carrier/Trane/Flaktwoods/ETA/ Voltas/Zeco/Caryaire/ Saiver/ Sin/VTS
3 | AHU Blowers |  | Nicotra /Comefri /Kruger / TCF Nadi
4 | VAV box |  | Trox / Titus/ Johnson controls / E H Price / Flaktwoods/System air Sweden/Aldes/Cosmos
5 | Centrifugal Fans |  | Nicotra /Comefri /Kruger /Systemair / Greenheck / TCF-Nadi / Flaktwoods
6 | Axial Fans |  | Nicotra/ Kruger / Nuaire/Greenheck/Flaktwoods /TCF-Nadi /System air
7 | Smoke extract/ Tube Axial /Axial/Centrifugal Fans |  | Systemair / Greenheck / Nuaire /Flaktwoods / Kruger/Nicotra
8 | Factory fabricated Ducts |  | Rolastar / Zeco / Alphaduct/Voltas/Spiraduct/Nutech
9 | GI Sheet |  | SAIL / TATA / Jindal (JSW)
10 | Air outlets - Grilles/ Diffusers |  | Dyna craft / Trox / Airmaster/ Titus -Caryaire / Cosmos
11 | Jet nozzle |  | Caryaire / Trox / Dynacraft
12 | Fire Damper with fusible link |  | Titus-caryaire / TSC/Ruskin / Cosmos / Air products/Greenheck
13 | Volume control Dampers |  | Ravistar /Airmaster/Caryaire(Flaktwoods)/Air products/ Cosmos / Dynacraft
14 | Flexible ducting |  | UP Twiga/Caryaire/Century mech systems
15 | Pipe Flexible Connectors (Bellow type) |  | Resistoflex / Easyflex/Cori
16 | Butterfly Valves |  | Audco / KITZ / Advance
17 | Ball Valves |  | Oventrop / RB / KITZ/ Kirloskar / Leader / Audco
18 | Gate Valves |  | Leader /Audco/RB / Zoloto
19 | Globe Valves |  | Leader /Audco/RB / Zoloto
20 | Check(NonReturn) Valves |  | Advance / Honeywell /Danfoss
21 | Manual Balancing valves |  | T & A / Advance / Danfoss / Oventrop / Honeywell
22 | Automatic Flow control valves |  | T & A / Flowcon / Danfoss / Oventrop / Advance
23 | Pressure independent dynamic balancing cum control valves/Differential pressure controllers |  | T & A / Danfoss /Oventrop/ Flowcon / Advance
24 | Thermostat with speed switch for FCU |  | Honeywell/Johnson control /Siemens/ Schneider (t.a.c)/ Sauter / Atmos
25 | Pressure Gauges |  | H.Guru / Fiebig / WAREE
26 | Pressure / temperature senors, Differential pressure,switch / Airflow switch |  | Honeywell/Siemens/Johnson control / Schneider (t.a.c.) / Atmos/Danfoss/Sauter
27 | Filters |  | Camfil Farr/ Promark/Purafil/Spectrum/Dyna/Airtech
28 | Air Curtains |  | Rusell/Airtech
29 | Catalytic Air Cleaner |  | Trane/ Bryaire
30 | Flexible Fibre Glass Blanket Insulation for ducting |  | U.P. Twiga/ Kimmco/Owens Corning
31 | Rigid preformed fiberglass pipe sections |  | U.P. Twiga/ Kimmco/Owens Corning
32 | Nitrile rubber duct/pipe insulation |  | Armaflex/K-flex/Rubatex
33 | Preformed PUF insulation sections for pipes |  | Lloyds insulation/Seven Star
34 | Preinsulated MS pipes |  | Lloyds insulation/Seven Star / Permapipe
35 | DDC controllers |  | Honeywell/Siemens/Danfoss/Johnson Controls/Sauter
Electrical
1 | 415 Volts, Main LT Panel, Motor Control Centre and APFC panel |  | L &T, S&W, Siemens, Schneider, ABB, Vivid, Electromech Pvt. Ltd., Tricolite, Legrand
2 | Indicating Lamps LED type and Push Button |  | Schneider Electric (MG), Larsen & Toubro (ESBEE), GE Power Controls, Siemens, Teknik, RAAS
3 | Overload relays with built in Single Phase preventer |  | Schneider Electric (Telemechanique), ABB, L&T, GE Power Controls, Siemens
4 | Electronic Digital Meters (A/V/PF/Hz/KW/KWH) with LED Display |  | Rishabh ( L&T), Enercon System Pvt. Ltd., CG Schlumberger, Automatic Electric, Schneider Electric
5 | Distribution Boards |  | L&T - Hager / Legrand / Siemens / Schneider
6 | Air Circuit Breaker |  | Schneider Electric (MG), ABB, Larsen & Toubro (U-Power),GE Power Controls (M-PRO), Siemens
7 | Molded Case Circuit Breaker (MCCB) |  | Schneider Electric (MG), ABB, Larsen & Toubro (U-Power),GE Power Controls (M-PRO), Siemens
8 | Miniature Circuit Breakers (MCB) |  | Schneider Electric (MG), Larsen & Toubro (Hagger), GE Power Controls (M-PRO), ABB, Siemens, MDS (Legrand)
9 | Residual Current Circuit Breaker (RCCB) |  | Schneider Electric (MG), Larsen & Toubro (Hagger), GE Power Controls (M-PRO), ABB, Siemens, MDS (Legrand)
10 | Power/Aux. Contactor |  | Schneider Electric (Telemechanique), Larsen & Toubro (Hagger), GE Power Controls , ABB, Siemens
11 | Change Over Switch |  | Larsen & Toubro, Siemens, H H Elcon, HPL-Socomec,Emerson
12 | Switch & Socket |  | Legrand (Mosiac), M K India, Northwest, Crabtree, Anchor, Gold Medal, Greatwide
13 | PVC insulated copper conductor stranded flexible wires (LSZH) - |  | Polycab, KEI, Finolex, Orbit, Kunth Cab, R R Kabel, Lapp Kabel, Delton Cables
14 | PVC insulated FRLS aluminium / copper conductor armoured / un armoured MV Cables up to 1100 V grade |  | Polycab, KEI, Orbit, Cable Corp. of India, RPG Cable, Fort Gloster, Kunth Cab, Ravin Cables
15 | Cable Trays (Factory Fabricated) / Raceways |  | Indiana, Profab Engineer, Jamana Metals, Rico Steel, Maheshwari Electrical Mfrs (MEM), Legrand
16 | Industrial Socket
| a. Splash Proof |  | Clipsal, Legrand, Neptune, Schneider Electric, Scane
| b. Metal Clad |  | BCH, Legrand, Schneider Electric
17 | Mettalic / GI Conduit (ISI approved) |  | BEC, AKG, Vimco, Steelkraft, Super Sales Corpn
18 | Accessories for Metallic Conduit (ISI approved) |  | Sharma Sales Corporation, Prakash Engineering Works, Super Sales Corporation
19 | Pop UP Box |  | WQ India, MDS Legrand, Fresar Techno
20 | High Power Fluorescent / General LED Lights |  | Philips, Wipro, Thorn, Crompton , Bajaj Electricals, Havells
21 | Ceiling Fan |  | Crompton Greaves, Usha, Orbit, Orient, Bajaj
22 | Exhaust Fan |  | Crompton Greaves, Usha, Almonard, Bajaj
23 | Shaver Socket |  | Clipsal, MK India
24 | LED General Area/ Office Lighting Utility buildings, etc. |  | Philips, Wipro, Surya, Crompton, Osram, Havells
25 | Lighting Controls |  | Dynalite, Schneider
26 | Bimettalic Cable Lug |  | Dowell's (Biller India Pvt. Ltd.), Comet, Hax Brass, Copper Alloy India Ltd.), Braco, Cosmos
27 | Cable and wire connectors upto 20 sq.mm |  | 3M, TE Connectivity, GE, Ideal Industries, Ashwin Electro ,Industrial Corporation, Novoflex
IT
1 | CCTV |  | DVTEL, Samsung, Pelco, Javelin, Philips, Vicon, Bosch, Infinova, Flair, for VMS - Milestone, Genetec
2 | Access Control |  | Bosch, Honeywell, Lenel
3 | Card Reader & proximity card |  | HID, Tyco Security, Honeywell security, wesinghouse
4 | Network cabling system (CAT6 cable & Fiber) |  | Compscope, Panduit, Beldon, Siemon-USA, Corning, Finolex, Orbit, R&M
5 | IT Rack, PDU & accessories |  | WQ India, Rittal India, Netrack, Valrack
6 | Speaker, Amplifier |  | Bose, Bosch, Aties, JBL
7 | Network Switches |  | Juniper, Cisco, Extreme, HP
8 | Cable/Fibre Connectors |  | Molex, Amphenol, Corning, Siemon, R&M
9 | Display Screen (FIDS) |  | Samsung, NEC, LG
Civil | Cement
1 | OrdineryOrdinary Portland Cement |  | Ultratech, ACC, Gujarat Ambuja, Grasim, JK Cement
2 | White Cement |  | Birla White, JK White, Ultratech White, Zuari White
3 | Ready Mix Concrete |  | ACC, Lafarge, RMC (Ready Mix India), Ultratech
4 | Rolling Shutters |  | Swastik, Gandhi Automation Pvt.Ltd., Shaktimet Hormann
5 | Autoclaved Aerated Concrete (AAC) /Light Weight Blocks |  | Hyderabad Industries Ltd., Siporex India Pvt.Ltd., Biltech Building Elements Ltd, JVS Comatsco Pvt.Ltd., Ultratech
6 | Integral Waterproofing compound |  | BASF, Fosroc, Sika, MYK Schomburg, Mc Bauchemei
7 | Membrane Waterproofing System |  | BASF, Fosroc, Sika, Grace
8 | Glasswool Insulation |  | Lloyds Insulation, UP Twiga, Owens Corning, US Gypsum (Boral)
9 | Acoustic Non-woven Fabric |  | Hunter Douglas, Soundtex, Owens Corning
10 | Underdeck Insulation |  | Lloyd Insulations (I) Pvt.Ltd., UP Twiga Fibre Glass Ltd., Bakelite Hylam Ltd.
11 | Extruded Aluminium Sections for Doors / Windows / Structural Glazing |  | Jindal Aluminium Ltd., Hindalco, Nalco, Indal, Bhoruka
12 | Glass (relevant code BS 952 & Selection as per AS 1288) Heat Strengthened Glass / Toughened Glass / Laminated Glass / Safety Glass / Annealed Glass |  | Saint Gobain (France), Shanghai Pilkington, China Southern Glass (CSG)
13 | Structural & Weather Sealant – Silicone Sealant |  | Dow Corning, GE, BASF, Alstone, Wacker
14 | Aluminum Composite Panels (ACP) |  | Aluco bond, Alpolic FR, Reynobond
15 | Ceramic Tiles |  | Johnson, Kajaria, Nitco, RAK Ceramics, Somany
16 | Double Charged / Anti-Skid Vitrified Tiles |  | Johnson, Kajaria, Nitco, RAK Ceramics, Somany
17 | Acid Resistant Tiles |  | Regency Ceramics Ltd., H & R Johnson (I) Ltd.
18 | Tile Adhesives & Grouts |  | Mapei, Laticrete, Ardex Endura, Pidilite, BASF, Fosroc
19 | Glass / Ceramic Mosaic Tiles |  | Glass Italia, Bizzaza, Palladio, Pixel, Shon
20 | Granite Stone Sealer |  | Laticrete, Aquamix, Ardex Endura, Sika
21 | Wooden Flooring |  | Xylos, Ego, Armstrong, BVG Industries
22 | Raised Access Flooring |  | Kingspan, Lindner, Unitile Raised Access Floor Systems, Bestlock System & Concepts, DMC, United Access Floor Ltd.,
23 | Plastic / Acrylic Emulsion Paint & Oil Bound Distemper |  | ICI, Berger, Asian Paints, Jotun, Nerolac
24 | Synthetic Enamel Paint (For building works) |  | ICI, Berger, Asian Paints, Shalimar, Kansai Nerolac, Spectrum
25 | Interior Grade Textured Paints |  | Asian Paints, ICI, Oikos, Jotun
26 | Epoxy & Polyurethane Paints / Coatings over Steel |  | ICI (Akzonobel), Asian Paints PPG, Berger, Jotun,
27 | Fire Retardant (Intumescent) Steel Protection System |  | Akzonobel, Jotun, Asian Paints PPG, Newkem Engineers
28 | Epoxy Coatings |  | BASF, Fosroc , Sika, Cipy
29 | Mineral Fibre False Ceiling |  | Armstrong, Saint Gobain, Knuaf AMF India Pvt.Ltd.
30 | Calcium Silicate False Ceiling |  | Hilux, Calsi Ceilings, Aerolite
31 | Gypsum Board Ceiling & Dry Wall Partitions |  | Saint Gobain, Lafarge, US Gypsum
32 | Plywood (Commercial / Marine Grade) |  | Century, Green Ply, Mayur, Kenwood
33 | MDF Boards |  | Nuchem Ltd., Mangalam Timber Products Ltd., Western Bio Systems Ltd., Bajaj Eco-Tec Products Ltd., Greenply
34 | Particle Boards (Plain / Veneered / Pre-laminated) |  | Merino, Century, Bajaj Eco-Tec Products Ltd.
35 | Laminates |  | Green Ply, Merino, Durian, Greenlam Industries, Formica India, Royale Touch
36 | Fire Rated and Non Fire Rated Steel Doors |  | Shakti Hormann, Godrej, Navair, Signum, Gmp, MPP Technologies
37 | Stainless Steel Hardware Fittings for Doors & Windows |  | Assa Abloy, Dorma, Ingersoll Rand
38 | Patch Fittings |  | Assa Abloy, Dorma
39 | Mirrors |  | Saint Gobain, Modi Glass, Asahi India