## Idli.Com
EQUIPMENT SCHEDULE
Idli.com @ SHA Departure
|  | Lucknow T3 | DATE | 2024-10-19
SR.No. | Eq.No. | DESCRIPTION | MODEL NO | DIMENSIONS(L x W x HT) | QTY | ELECTRIC SUPPLY 3PH/1PH | Per Kw | TOTAL KW | AMPS | TYPE OF SWITCH | Comments -SKPL | EXHAUST CFM
FOH-IDLI.COM
3 | ID-03 | JUICE DISPENSER | UGOLININ-DELUX 12/2 | 360 x 480 x 570Ht, | 1 | 1PH | 1 | 1 | 5 / 15 Amp | Switch Socket
4 | ID-04 | FLOOR MOUNTED HOT BAIN MARIE WITH 3Nos.1/1x150Deep GN PAN WITH EXTERNAL PANEL | FABRICATED | 1125 x 650 x 850 | 1 | 1PH | 3 | 3 | 32 | Metal Clad | As per layout it is 3 nos 1/1 GN Bain Marie, Length to be 1125mm
5 | ID-05 | Cold BAIN MARIE WITH 1 Nos. OF 1/1 GN PANS 200mm DEEP | FABRICATED | 450 x 650 x850 | 1 | 1PH | 0.5 | 0.5 | 5 / 15 Amp |  | As per layout this is Cold Bain Marie. Revise length to 450mm
6 | ID-06 | GAS OPERATED FLOOR MOUNTED HOT PLATE WITH 1 U/S LEG OFFSET FROM BACK SIDE & Right SIDE 150MM | FABRICATED | 900 x 650 x 850 | 2 | [5 empty] | Qty - 2 nos. Electrical Point not required.
7 | ID-07 | AMBIENT BAIN MARIE WITH 6 Nos. OF 1/6 GN PANS 200mm DEEP | FABRICATED | 450 x 650 x850 | 1 | [5 empty] | Length to be 450mm
8 | ID-08 | BOX TYPE EXHAUST HOOD WITH BAFFLE FILTERS & FIRE SUPPRESSION SYSTEM , FRESHER GRILL & LED LIGHTS-(1200CFM) | FABRICATED | 2290 x 950 x 500 | 1 | 1HP | 1 | 1 | 5 / 15 Amp | Switch Socket | Length to be 2290x950x500
9 | ID-09 | BOX TYPE EXHAUST HOOD WITH BAFFLE FILTERS & FIRE SUPPRESSION SYSTEM , FRESHER GRILL & LED LIGHTS-(1100CFM) | FABRICATED | 850 x 950 x 500 | 1 | 1HP | 1 | 1 | 5 / 15 Amp | Switch Socket | Length to be 850x950x500
10 | ID-10 | Combi Oven Unox (Gas operated) | UNOX Model - XEVC-1011-GPRM | 750 x 783 x 1010Ht. | 1 | 1HP | 18.5 | 18.5 | 32 | Switch Socket | Gas operated Model - XEVC-1011-GPRM
11 | ID-10 A | SS Table with 2 U/S | FABRICATED | 800 X 770 X 850Ht. | 1
12 | ID-11 | 2 DOOR UNDER COUNTER CHILLER | BLUE STAR-UC2100GC | 1365 x 700 x 850ht | 2 | 1PH | 3 | 3 | 5 / 15 Amp | Metal Clad | Qty 2 Nos, Electrical Point should be 5/15 Amp and load to be 1KW.
14 | ID-13 | FILTER COFFEE MACHINE-2Ltrs Cap. | GEMINI-2000 | 220 x 390 x 600Ht. | 1 | 1PH | 2 | 2 | 5 / 15 Amp | Switch Socket
15 | ID-14 | MILK BOILER INSULATED - 12Ltrs.Cap. | PRADEEP - 111612 | 320DIA x 580Ht. | 1 | 1PH | 1.5 | 1.5 | 5 / 15 Amp | Switch Socket
16 | ID-15 | TEA KETTLE MACHINE - 12Ltrs.Cap. | PRADEEP - 111313 | 320DIA x 580Ht. | 1 | 1PH | 1.5 | 1.5 | 5 / 15 Amp | Switch Socket
17 | ID-16 | MICROWAVE OVEN | CELFROST-CMO25 | 511 x 432 x 311Ht. | 1 | 1HP | 1.9 | #REF! | 5 / 15 Amp | Switch Socket | 5 / 15 Amp switch socket
19 | ID-18 | GREASE TRAP | NUGREEN-NGT-14 | 355 x 262 x 280Ht. | 1
23 | ID-22 | FOOT OPERATED HAND WASH SINK WITH HOT & COLD WATER CONNECTION & WITH TISSUE HOLDER & SOAP DISPENSER PROVISION | FABRIATED | 500 x 475 x 850+450 | 1
Total Kw-A IDLI.COM FOH | [7 empty] | #REF!
Total Kw-B- BACK KITCHEN
SOE
1 | SO-01 | RO SYSTEM | SOE (AS PER MEP) | 100lph wall mounted unit with SS Stand. All Accessories included (Booster Pump, Auto cut-of Tank valve, etc) | 1 | AS PER MEP
3 | SO-03 | INSECT KILLERS | SOE |  | 2 | 1PH | 0.5 | 1 | 5 / 15 Amp
Total Kw-D SOE | [7 empty] | 1
Total (Kw) A+B | [7 empty] | #REF! |  |  |  | 0