## Summary
MEET & GREET KIOSK CITY SIDE CANOPY AREA
SUMMARY FOR INTERNAL ELECTRIFICATION WORKS
Sl No. | AREA | AMOUNT | REMARKS
1 | DBS SYSTEM | 0
2 | LT CABLES | 0
3 | WIRING SYSTEM (INTERNAL) | 0
4 | EARTHING SYSTEM | 0
| TOTAL | 0
| SAY | 0
Lights cost not considered in this BOQ.

## BOQ-Proj
MEET & GREET KIOSK CITY SIDE CANOPY AREA
ESTIMATE FOR INTERNAL ELECTRIFICATION WORKS
SL. NO | ITEM OF WORK | UNIT | QTY | RATE | AMOUNT | REMARKS
|  |  |  | (Rs/unit) | (Rs.)
1 | DISTRIBUTION BOARD
1.1 | Supplying and fixing of following ways surface/ recess mounting, vertical or horizontal type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 100 A, tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required. Make: Legrand / Schneider / Hager / ABB
a | 6 way (8 + 18), Double door | Each | 0 |  | 0 |  | LPDB
1.2 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, inter- connections, powder painted including earthing etc. as required. (But without MCB / RCCB / Isolator) Make: Legrand / Schneider / Hager / ABB
a | 6 way , Double door | Each | 1 |  | 0 |  | UDB
1.4 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make: Legrand / Schneider / Hager / ABB
a | Single pole | Each | 4 |  | 0 |  | DB's outgoing MCBs
b | Double pole | Each | 0 |  | 0 |  | incomer of UDB
1.5 | Supplying and fixing following rating, Four pole, (three phase and neutral), 415 V, Residual Current Breaker with Over-Current (RCBO), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make: Legrand / Schneider / Hager / ABB
a | 63A 4P RCBO | Each | 0 |  | 0 |  | incomer of LPDB
1.6 | Supplying and fixing following rating, Four pole, (three phase and neutral), 230 V, Residual Current Breaker with Over-Current (RCBO), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make: Legrand / Schneider / Hager / ABB
a | 25A 2P RCBO | Each | 1 |  | 0 |  | incomer of LPDB
1.7 | Supplying and fixing following rating, four pole, 415 V, MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make: Legrand / Schneider / Hager / ABB
a | 40A FP MCB | Each | 0 |  | 0
| SUB TOTAL MDBS / DBS SYSTEM |  |  |  | 0
2 | L T CABLE SYSTEM :
2.1 | S.I.T.C. 1100Volts grade cable as per I S: 7098, pt.1 (latest edition) with stranded copper conductor; XLPE insulated, multi-core, bunched, armoured with overall heat resistant type ST-2 PVC insulation / Copper stranded conductor; PVC insulated as per I S: 1554 (latest edition). Cable shall have nominal identification plates at booth ends ('supply from' & ;supply to') & with end termination as required at site. The sizes are as follows:
a | : 4C x 16 sq. mm. 2XWY | Mtr. | 0 |  | 0
b | : 3C x 4 sq. mm. 2XWY | Mtr. | 0 |  | 0 |  | DB incomer cable / Qty - Distance need to check at site from Existing Panel to Our Floor DB.
| SUB TOTAL L T CABLE SYSTEM : |  |  |  | 0
3 | WIRING SYSTEM (Internal wiring) :
3.1 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | Metre | 5 |  | 0 |  | Lighting Wiring from DB Board to Sw Board
3.2 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 2x1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1x1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required.
a | Point Wiring | No | 3 |  | 0 |  | Lighting Wiring from Sw Board to all lights
POWER POINTS :
3.3 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
a | 2 X 4 sq. mm + 1 X 2.5 sq. mm earth wire (for Power circuit & loop-in-out) | Metre | 20 |  | 0 |  | Lighting Wiring from DB Board to all sockets
3.4 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 13/6 amps modular universal socket outlet and 13/6 amps modular switch, connection etc. as required. | Each | 4 |  | 0 |  | 6A socket
3.5 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 5/16 amps modular socket outlet and 16 amps modular switch, connection etc. as required. | Each | 0 |  | 0 |  | 16A socket Normal
3.6 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing Cat6A modular socket, connection etc. as required. (for data & telephone) | Each | 3 |  | 0 |  | Lan Socket
| Sub Total WIRING SYSTEM (Internal wiring) : |  |  |  | 0
4 | EARTHING SYSTEM
4.1 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | Mtr | 0 |  | 0 |  | along with DB incomer cable / to be loop from existing earth bus at site.
| Sub Total - Earthing System |  |  |  | 0
| TOTAL |  |  |  | 0