## HIGH SIDE
NAME OF PROJECT: LKO FOOD HALL AT LUCKNOW
HVAC WORK (HIGH SIDE)
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
A | EQUIPMENTS |  |  | RATE |  | AMOUNT
1 | Ceiling Suspended AHU
Supplying, installing, testing and commissioning of double skin construction draw thru type Ceiling Suspended AIR HANDLING UNITS as per specification, each complete with ESP Filter (94% down to 3 microns), pre-filter section (90% down to 10 microns), min 6 Row Deep Chilled water coil of copper tube & aluminium fins construction, squirrel cage induction motor, airfoil centrifugal fan belt drive and vibration isolators, coil size shall be selected for a maximum face velocity of 500 feet/minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (IE2) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Fan motor assembly (as whole) shall be statically and dynamically balanced to grade G 6.3 as per ISO-1940/AMCA 204-3.All units shall be complete with opposed blade volume control dampers at oulet. Duct flexible connector (fire proof) shall be provided at outlets of AHU. ( Temporary bypass arrangement in Chilled Water Line with related accessories to be considered to facilitate flushing during precommissioning and commissioning of the System).
AHU Tag. Description AHU CFM TR ESP Motor HP
| AHU-01 Sitting area 2500 cfm 5 15 mm 2 | No. | 1
TOTAL
GRAND TOTAL (SUPPLY + INSTALLATION)

## MAKE LIST
NAME OF PROJECT: LKO FOOD HALL AT LUCKNOW
HVAC APPROVED MAKES LIST
Sr. No. | Details of Materials / Equipment | Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | Air Handling Unit | Zeco/ Edgetech / Carrier/ Blue star / Waves
9 | M.S. Pipe upto 200 MM Dia. | AST / Jindal Hissar / Prakash Surya /Tata Steel
10 | UPVC Drain Piping | Prince / Supreme
11 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
12 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
13 | Duct Thermal & Acoustic Insulation | Thermobreak / Supreme/ ARMACELL
14 | Closed Cell Nitrile Rubber along with adhesive | Armaflex / K-flex/ ARMACELL
15 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
16 | Cables | Polycab / Finolex / Hawells
17 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
18 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
19 | ESP Filter | Honeywell/Magneto/Trion
20 | Ball valve | Honeywell/Zoloto/Emerald /Advance Valve /Navtech (Castle
21 | Y Strainer | Emerald / Rapidcool
22 | Pressure Gauge | Emerald /Fiebig /H Guru
23 | Thermometer | Emerald /Fiebig /H Guru
24 | Auto Air Vent Valve | RB / Rapid Control
25 | PIBCV for AHU | Belimo / Danfoss / Honeywell / Schneider / Siemens
26 | Room Thermostat | Danfoss / Honeywell / Schneider / Siemens
27 | Starter | Siemens / Allen Bradley/ ABB / Schneider / L & T
28 | BTU Meter | Johnson Control / Honeywell / Kamstrup / Landis Gyr