## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
13 | FIRE DETECTION AND ALARM SYSTEM
13.1 | Automatic Floating Sensitivity type Analog addressable Acclimate Multi-criteria smoke detector with mounting based LED, Address Switch from 01-159 , to programme the detectors, . (In Changing Environment Area) as per the specifications | Nos. |  | R.O
13.2 | Analog addressable Rate of Rise Cum Fixed temperature detector with mounting based LED, Address Switch from 01-159 , to programme the detectors complete as required. | Nos. |  | R.O
13.3 | Supply, installation, testing & commissioning of addressable control modules for driving outputs like Hooters, fire Damper,controlling zones of speakers etc. complete as required and as per specification.(For Airwasher & Dry Scrubber) | No. |  | R.O
13.4 | Supply, installation, testing and commissioning of Manual Call Points Addressable Type, flush monted in partition or concealed in wall for manual actuation in case of fire. | Nos. | 1
13.5 | Supply, installation, fixing, testing and commissioning of Strobe Lights Cum Hooter with 110 cd. The strobes shall be synchronized for better evacuation. | Nos. | 1
13.6 | Supply, installation, testing and commissioning of response indicators suitable for above smoke detector complete with M.S. junction box top hylum sheet and required accessories. | Nos. |  | R.O
13.7 | Supply and drawing of 2c x 1.5 sq.mm copper cable, 2 cores twisted together, armored, such that the cable retains Circuit Integrity for minimum 2 hours at a service voltage of up to 1000V under SIMULTANEOUS ACTION of flame at 950°C, Mechanical Shocks and Water Stress with all these 3 being performed on the same cable sample. The cable should also have Light Transmittance as per IEC-61034. 3rd Inspection report shall be submitted with every Lot. | RM | 30
13.8 | Supplying and fixing of following sizes of MS conduit alongwith the accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a) | 25 mm dia MS conduit | RM | 0
b) | 20 mm dia PVC flexible conduit | RM | 30