## ELECTRICAL
KFC Food Court Ahmedabad Airport.
Estimated Cost - Electrical Works Dated 29th Feb. 2024
The prices are to be quoted in the section mentioned below and shall include the supply, Installation, Testing and commissioning at site of all the equipments, ancillary materials as specified and all such items what so ever required to fulfill the intent and purpose as laid down in the specifications and/or drawings and shall include all taxes and duties on works contract basis.
S. No. | Description | Unit | Qty. | Rate | Amount
|  |  |  | (Rs.) | (Rs.)
Design, fabrication, assembling, wiring , supply , Erection , Installation , testing and commissioning of MDB Panels fabricated out of 2mm thick for structural members (Load bearing members) and 1.6mm thick for door and covers (Non load bearing members) CRCA painted sheet steel in cubicle formation with reinforcement of suitable size angle iron, channels, T irons, flats wherever necessary for large meter boards. Cable gland plates shall be provided at top and bottom both and windows for meter reading, locking arrangement (pad-lock & seal) with wiring upto KWH meter & meter to MCB shall be done by using adequately rated flexible single core copper wire. The boards shall be treated with all anticorrosive process before painting as per standards with final approved shade of powder coated as approved, 2 nos. earthing terminals shall be provided for all panels. The boards shall be suitable for 415 V, 3 phase, 4 wire, 50 Hz supply system. Boards shall be fabricated in length, height, depth etc to match with site conditions.
An approval shall be taken for each panel before manufacturing. Galvanised hardwares with zinc passivation shall be used in fabrication of boards.
Note: The following provisions shall be required to be made in the switchboard detailed below
The Switchboard shall have provision for entry of all PVCA cables from the top/bottom as required.
All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The busbar insulation shall be with heat shrinkable sleeves. SMC/DMC shrouds and busbar supports shall be used.
Suitable tinned copper extension links for incoming/outgoing cables shall be provided wherever required
Control circuits includes breaker control switch, auto manual selector switch, anti pumping relay, spring charging trip indication, TIMER, control wiring, Auxiliary contactors MCB’s as required at site.
Positive isolation of all breakers.
All fault level breaking capacity indicates shall be ICS value at 415 volts (ICS = ICU = ICW = 100%).
Space Heater/ light/air filter shall be provided for each vertical compartment
Link and drops from MCCB shall be designed for full rated current of MCCB ratings at same current density as of Main Bus Bar
2 nos. GI earth strip throughout the panel.
1 | MAIN Panel
A | Incoming
1 No. 160 amps 16 kA 440 volt FP MCCB with Thermal Magnetic overcurrent and short circuit and with following
B | Metering, Indication & Protection:
a | 1 Nos. 6 Parameter Multi Function Mater with 3 Nos. Cast Resin CTs and MCBs
b | Breaker ON OFF indication Lamps
c | R-Y-B indication lamps with MCBs
d | ELR with CBCT
C | Bus Bar:
200 A, TPN Al. Bus Bar of suitable length having Current density 1Amp/sq.mm & having high conductivity electrical grade suitable to withstand symmetrical fault level of 25 kA. Neutral busbar shall be of 100% capacity.
D | Outgoings:
a | 3 No. 63 amps 4P MCB ( Type C)
b | 5 No. 25 amps 4P MCB ( Type C)
c | 7 No. 32 amps 2P MCB ( Type C)
d | 1 No. 25 amps 2P MCB ( Type C)
| Main MDB as described above | 1 | Set | 190000 | 190000
1.1 | DISTRIBUTION BOARDS
Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects.
Note : All MCBs in distribuition board for power circuits shall be of C curve
i | Type A
| 1-63 amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(100 mA) and 6 nos. 6/16/20/25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | 2 | Set | 24000 | 48000
ii | Type B
| 1-32 amp DP MCB + DP RCCB ( 100mA) and 12 nos. 6/16/20/25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | 1 | Set | 12000 | 12000
ii | Type C
| 1-32 amp DP MCB + DP RCCB ( 100mA) and 8 nos. 6/16/20/25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | 2 | Set | 9500 | 19000
iv | Type D
| 1-25 amp DP MCB + DP RCCB ( 100mA) and 6 nos. 6/16/20/25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | RO | Set | 8500
2 | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as required | 2 | No. | 45000 | 90000
3 | Supply, laying, testing & commissioning of following sizes of Al/Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables/ Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O/H cable tray, on wall as required )
3.1 | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable * | 40 | Mtrs | 1200 | 48000
3.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable | 70 | Mtrs | 400 | 28000
3.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | 30 | Mtrs | 350 | 10500
* Approximate and shall be as per point of supply from Airport Panel/ Isolator
4 | Supply, erection, testing & commissioning of following sizes of cable end terminations with Single compression gland for 1.1 kV grade, XLPE insulated, Al/Cu Conductor cable
4.1 | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable *(Double Compression) | 2 | Nos. | 2200 | 4400
4.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable | 6 | Nos. | 800 | 4800
4.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | 4 | Nos. | 450 | 1800
5 | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface/concealed MS surface/concealed conduit including cost of providing saddles etc as required for surface conduiting and/or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below
5.1 | 4 x 16 sq.mm + 2 No. 6.0 Sq. mm in 40 mm dia MS Conduit | 35 | Mtrs | 1250 | 43750
5.2 | 4 x 6 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit | 10 | Mtrs | 950 | 9500
5.3 | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit | 75 | Mtrs | 475 | 35625
5.4 | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit | 280 | Mtrs | 350 | 98000
6 | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts/ in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043:1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required
6.1 | 50X6 mm GI Strip | 15 | Mtrs | 450 | 6750
6.2 | 25X6 mm GI Strip | 20 | Mtrs | 325 | 6500
6.3 | 25X3 mm GI Strip | 30 | Mtrs | 200 | 6000
6.4 | 8 SWG Copper Wire | 70 | Mtrs | 90 | 6300
6.5 | 8 SWG GI Wire | 100 | Mtrs | 25 | 2500
6.6 | 1 Core 6.0 Sq. Mm FRLS Green Wire | 60 | Mtrs | 65 | 3900
7 | Supply, erection, testing & commissioning of prefabricated GI Perforated type cable trays including Tees / Bends / Crossing / Reducers / Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as required including support at every 1500mm as required
7.1 | 150 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip | 30 | Mtrs | 700 | 21000
7.2 | 300 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip | 15 | Mtrs | 1100 | 16500
7.3 | 450 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip | 10 | Mtrs | 1400 | 14000
8 | Wiring for MCB controlled normal primary light points/ Wall Point/ Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall / ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | 4 | Pt | 2500 | 10000
9 | Wiring for secondary MCB controlled normal light points/ Wall Point/ Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall / ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | 10 | Pt | 1000 | 10000
10 | Wiring for MCB controlled Emergency primary light points/ Wall Point/ Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall / ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | 1 | Pt | 3000 | 3000
11 | Wiring for secondary MCB controlled Emergency light points/ Wall Point/ Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall / ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | 6 | Pt | 1500 | 9000
12 | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall / ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect / Client) | 8 | Pt. | 2000 | 16000
13 | Wiring same as in Item 12 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI boxes with internal wiring and moulded front plates complete as required. ( Switch and socket shall be as approved by the architect / Client) | 12 | Pt. | 1200 | 14400
14 | Same as above but switch and socket provided at separate location including wiring berween switch and socket and complete as required | RO | Pt.
15 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall / Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect / Client) | 6 | Pt. | 2800 | 16800
16 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall / Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect / Client) | 5 | Pt. | 3250 | 16250
17 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall / Ceiling including cost of providing saddles etc as required for surface conduiting and/or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch/Socket Shall be as per approved sample by Architect) | 4 | Pt. | 4200 | 16800
18 | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall / Ceiling including cost of providing saddles etc as required for surface conduiting and/or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A modular switch , safety shutters in a recessed/surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch/Socket Shall be as per approved sample by Architect) Note- Conduits shall be 16 SWG MS on surface and FRLS PVC for wall concealed | 5 | Pt. | 4500 | 22500
19 | Supply installation testing and fixing 3 pin 16A/20A , 240V , single Phase metal Clad industrial socket outlet with 16A/20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | 21 | Nos. | 3200 | 67200
20 | Supply installation testing and fixing 3 pin 25A/32A , 240V , single Phase metal Clad industrial socket outlet with 25A/32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | 6 | Nos. | 3500 | 21000
21 | Supply installation testing and fixing 3 pin 40A , 240V , single Phase metal Clad industrial socket outlet with 40A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | RO | Nos. | 4500
22 | Supply installation testing and fixing 5 pin 32A , 415V , single Phase metal Clad industrial socket outlet with 32A FP MCB and complete in all respects( Wiring Excluded from scope of this item) | 1 | Nos. | 6000 | 6000
23 | Supply , fixing & Laying 2.0mm Thick FRLS PVC conduits on surface or concealed complete with PVC junction boxes, cover plates, PVC bends, PVC saddles, base and other accessories all made in PVC with GI screws as required to complete the job. .
i | 25 mm dia FRLS PVC conduit | 30 | Mtrs | 85 | 2550
ii | 20 mm dia FRLS PVC conduit | 60 | Mtrs | 65 | 3900
24 | Supply , fixing & Laying 16 SWG MS conduits on surface or concealed complete with PVC junction boxes, cover plates, bends, saddles, base and other accessories all made in PVC with GI screws as required to complete the job. .
i | 25 mm dia 16 SWG MS conduit | RO | Mtrs | 180
ii | 20 mm dia 16 SWG MS conduit | RO | Mtrs | 160
25 | Supply and Installation of following in wall mounted MS enclosure
i | 32A/25A FP RCBO | 2 | Nos | 3000 | 6000
ii | 32A/25A DP RCBO | 5 | Nos | 1500 | 7500
26 | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover / blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring.
i | Single outlet face plate with RJ-45 Jack with information outlet | 16 | Nos. | 800 | 12800
ii | Duplex outlet face plate with RJ-45 Jack with information outlet | 4 | Nos. | 1500 | 6000
27 | Supply,installtion testing and commisioning of Cat-6A UTP cables in existing Conduit complete as required for Telephone and Data System | 200 | Mtrs | 55 | 11000
28 | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. | 22 | Nos | 250 | 5500
29 | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. | 22 | Nos | 325 | 7150
30 | Installation of following light fixtures including connections and complete in all respects
i | 25/15/12Watt Recessed Down Lighter | 7 | No. | 150 | 1050
ii | Signage | 2 | No. | 250 | 500
iii | 2X20W FTL LED | 11 | No. | 150 | 1650
Total For Electrical Works - INR |  |  |  |  | 831375
THE ABOVE EXCLUDES THE FOLLOWING:-
1 | Equipment ( Server , Ports etc) for networking / LAN system / EPABX and Centrex system , however infrastructure like Conduits / Pipes /RJ-45 sockets have been considered
2 | Fire Alarm System
3 | Supply of light fixtures. However installation and Wiring considered