## Summ
BILL OF QUANTITY FOR ELECTRICAL WORK OF PROPOSED OFFICE BOH @ TFS T1 DIAL
SUMMARY OF COST OF INTERIOR-ELECTRICAL WORK
SR. | DESCRIPTION | TENDER AMOUNT (Rs.)
NO. | OF ITEM |  | MAT. | INST. | TOTAL
1 | DBs | Rs. | 0 | 0 | 0
2 | CABLES | Rs. | 0 | 0 | 0
3 | POINT WIRING | Rs. | 0 | 0 | 0
4 | CABLE TRAYS & TRUNKINGS | Rs. | 0 | 0 | 0
5 | LIGHT FIXTURES | Rs. | 0 | 0 | 0
6 | EARTHING : | Rs. | 0 | 0 | 0
7 | Miscellaneous Item | Rs. | 0 | 0 | 0
8 | Fire Detection System | Rs. | 0 | 0 | 0
9 | CCTV System | Rs. | 0 | 0 | 0
10 | Telephone System | Rs. | 0 | 0 | 0
| TOTAL | Rs. | 0 | 0 | 0

## TENDER BOQ
BILL OF QUANTITY FOR ELECTRICAL WORK OF PROPOSED OFFICE INTERIOR OF BOH @ TFS T1 DIAL
TENDER BOQ.
SR. | DESCRIPTION OF ITEM | UNIT | TEN. | UNIT RATE (Rs.) |  |  | AMOUNT (Rs.)
NO. |  |  | QTY | MAT. | INST. | TOTAL | MAT. | INST. | TOTAL
1 | DBs
1.1 | Suply and installation of Four -Tier, Multi-Way, TPN,
Distribution Board for Lighting & Power distribution, surface
mounted on wall, sheet metal fabricated,powder coated,
having dust-proof and vermin 'proof, gasketed and hinged
acrylic door with all internals such as DIN rails, neutral-link,
interconnected wiring complete with earthing lugs housing
switchgears: (IP-43 with Metal Door)
1.1.1 | LIGHTING & POWER DB (6 way TPN DB)
a) 1 No., 32A, 4P MCB (INCOMER)
b) 1 No., 16A, 4P MCB (SUB INCOMER)
c) 3 Nos., 32A, DP, ELCB(30mA) Incomer(One per phase)
d) 12 Nos, 10A, SP, MCB outgoing
(Make: Legrand-Ekinoxe /Hager/Schneider
| Full Set as above | Set | 1 |  |  |  | 0 | 0 | 0
1.1.2 | UPS DB (12 way SPN)
a) 1 No., 32 A DP RCBO
b) 10 Nos, 16A, SP, MCB outgoing
(Make: Legrand-Ekinoxe /Hager/Schneider
| Full Set as above | Set | 1 |  |  |  | 0 | 0 | 0
| Sub Total of 1.0 | [5 empty] | 0 | 0 | 0
2 | CABLES :
2.1 | S & I of 1100V grade armoured/unarmoured/flexible cable
having sector / circular shaped Aluminum/copper conductor,
XLPE insulated cores, laid up, PVC tape wrapped,
inner sheathed, GI strip / wire armoured and overall
extruded FRLS PVC sheathed confirming to IS: IS:1554/ IS:7098/
IS:694, laid on Cable Trays /wall /ceiling including the
clamps & spacers required as per route in the drawing and
further as directed at site in the following sizes:
2.1.1 | 3R x 1C x 4 Sq.mm, Copper, Flexible, Bunched together - FROM UPS TO UPSDB | mtr. | 15
2.1.2 | 4 C x 6 Sq.mm, Copper, Armoured cable - FOR LPDB | mtr. | 35 |  |  |  | 0 | 0 | 0
2.1.3 | 4 C x 2.5Sq.mm, Copper, Armoured cable - FOR AHU | mtr. | 25 |  |  |  | 0 | 0 | 0
2.1.4 | 3 C x 4.0Sq.mm, Copper, Armoured cable- FROM LPDB TO UPS | mtr. | 15 |  |  |  | 0 | 0 | 0
2.1.5 | 3 C x 2.5 Sq.mm, Copper, Armoured cable FOR ELV SERVICES | mtr. | 20 |  |  |  | 0 | 0 | 0
2.2 | S & I of End Termination of above mentioned cables
including compressed type brass gland, crimping type
copper lugs, insulation tape etc. as 'required complete
with earthing of glands where ever required
2.2.1 | 3R x 1C x 4 Sq.mm, Copper, Flexible, Bunched together - FROM UPS TO UPSDB | Nos | 2
2.2.2 | 4 C x 6 Sq.mm, Copper, Armoured cable - FOR LPDB | Nos | 2
2.2.3 | 4 C x 2.5Sq.mm, Copper, Armoured cable - FOR AHU | Nos | 2
2.2.4 | 3 C x 4.0Sq.mm, Copper, Armoured cable- FROM LPDB TO UPS | Nos | 2
2.2.5 | 3 C x 2.5 Sq.mm, Copper, Armoured cable FOR ELV SERVICES | Nos | 2
| Sub Total of 2.0 | [5 empty] | 0 | 0 | 0
3 | POINT WIRING :
3.1 | Supply & Installation of concealed point wiring using 1100V grade 2.5 sqmm copper conductor PVC insulated wires (with proper R,Y,B color code ) pulled through PVC MMS conduits (including flexible conduits for drops to light fittings) laid concealed over false ceiling or in wall chases including circuit wires from the relevant SB and also including insulated green color copper earth wire for each circuit and providing modular grid plate type switches,sockets etc. as required. Each light point to be terminated using 5A connector or 5A two pin female socket (for cove lighting) as directed at site. Each circuit feeding not more than 12 points/800 watts as per following configuration:(LDBs located at two locations as shown)
3.1.1 | Wiring for the Primary light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in PVC conduits in F.ceiling/walls/ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. Rates shall exclusive of Switches & Switch boxes. (Lighting Circuit-Normal) | Mtr. | 20
3.1.5 | Wiring with 3R x 1.5 Sq.mm for 5A Plug points on wall/skirting etc. for general purpose through existing Raceway (Circuit shall be taken from the PDBs . Only 4 points looped in one circuit) (Conduits shall be paid separately) | Mtr. | 50
3.1.6 | Wiring with 3R x 2.5 Sq.mm for 15A Plug points on wall/skirting etc. for general purpose through existing Raceway (Circuit shall be taken from the PDBs . Only 4 points looped in one circuit) (Conduits shall be paid separately) | Mtr. | 25 |  |  |  | 0 | 0 | 0
3.1.7 | S & I of point wiring for Computer Power plug points on | Mtr. | 25 |  |  |  | 0 | 0 | 0
workstations / table for computers using 3C X 2.5 Sqmm
copper conductor PVC sheathed white color flexible cable
pulled through already laid floor raceways and taken
upto table top using metal rigid or flexible conduits run within
partitions.Each point consisting of 3 nos.of international
sockets controlled by 1no 16A, switch located below the table
wired together forming one point including back-boxes.
The earth wire of 3 core flexible cable to be of yellow-green color
only. Cost to include white colour flexible cable
+ flex conduit. Each table to be taken as one point.
(Max. 4/6 tables served by one circiut from UPSDB)
3.2 | S & I of 5A Raw,Power point wiring for points on workstations / table for Mobile charger using 3C X 1.5 Sqmm copper conductor PVC sheathed Black color flexible cable pulled through already laid floor raceways and taken upto table top using PVC rigid or flexible conduits run with in partitions.Each point consisting of 1 No 6A sockets controlled by 1no 5A,switch The earth wire of 3 core flexible cable to be of yellow-green color only. Cost to include white colour flexible cable + flex conduit. ( Six tables served by one circiut from LPDB) | Mtr. | 25 |  |  |  | 0 | 0 | 0
3.3 | S & I of PVC conduits including all
accessories, clamps, spacers, bends, tee, cross etc.
as required at site for miscellaneous use in following sizes:
3.3.1 | 20mm dia | Mtr | RO
3.3.2 | 25mm dia | Mtr | 50 |  |  |  | 0 | 0 | 0
3.4 | S & I of flexible PVC conduits including all
accessories, clamps, spacers, end adopters (Glands) etc.
as required at site in following sizes:
3.4.1 | 20mm dia | Mtr | RO
3.4.2 | 25mm dia | Mtr | 50 |  |  |  | 0 | 0 | 0
3.5 | Supply, Installation testing and commission of 240V-AC, wiring devices and its accessories such as modular type switch socket outlets with modular front plate, modular box, G.I. back box and all required accessories etc. Supply & Installation scope includes all civil works related to this job such as chiselling , making good with concrete and plaster, supply of fixing screw / wall plugs and other necessary hardware, marking identification numbers of circuits & interconnections of the switch /sockets as per standard drawing, complete as per site requirement. Switches and sockets may be individual or combined with bigger lighting switchboards, contractor to refer drawings to understand exact scope of work. LEGRAND - MYRIUS SERIES
1 | 6A One way plate type switch (Provision) | Nos. | 7 |  |  |  | 0 | 0 | 0
2 | 6A 5pin switch socket outlet (Raw power / UPS) | Nos. | 10 |  |  |  | 0 | 0 | 0
3 | 3 nos. 6/13A Flat pin Universal socket & 1no. 16A switch with indicatior (UPS power) | Sets | 7 |  |  |  | 0 | 0 | 0
4 | 13A Flat pin Universal switch socket outlet ( Raw Power/UPS ) | Nos. | RO
5 | 6/16A switch socket outlet ( Raw Power/UPS ) | Nos. | 5 |  |  |  | 0 | 0 | 0
6 | 6/16A switch socket outlet with indication ( Raw Power/UPS) | Nos. | 5 |  |  |  | 0 | 0 | 0
7 | data cum telephone back GI BACK box 2”x2” suitable for data socket | Nos. | 15 |  |  |  | 0 | 0 | 0
| Sub Total of 3.0 | [5 empty] | 0 | 0 | 0
4 | RACEWAYS & CABLE TRAYS :
4.1 | S & I of trunking same as above but of size 100mm x 38mm | Mtr | 0 |  |  |  | 0 | 0 | 0
x1.6 mm for power/data cables.
(PROFAB/ASIAN/Approved equivalent)
4.2 | S & I of trunking same as above but of size 68mm x 38mm | Mtr | 50
x1.6 mm thick for power/data cables.
(PROFAB/ASIAN/Approved equivalent)
4.3 | S & I of floor raceways similar to above but consisting 1 Run x 25mm dia, PVC Conduit pipe medium guage | Mtr | 0 |  |  |  | 0 | 0 | 0
4.4 | S & I of floor junction boxes similar to above but size 450mm x 450mm x 60 mm | Nos | 0
4.5 | S & I of floor junction boxes similar to above but size 350mm x 350mm x 60 mm | Nos | 0
4.6 | S & I of floor junction boxes similar to above but size 250mm x 250mm x 60 mm | Nos | 0
4.7 | S & I of floor junction boxes similar to above but size 150mm x 150mm x 60 mm | Nos | 0
4.8 | S & I of GI Pregalvanizd Perforated type Cable Tay
of following sizes suspended from ceiling or fixed
vertically on wall/column as per route directed at site
including all necessary bends, tees, crosses and also
including all necessary supporting arrangement.
All supporting hardware including nuts, bolts etc.
shall be also of galvanised M.S. as approved
(PROFAB/INDIANA/ASIAN/approved equivalent)
4.8.1 | 100mm x 50mm X 1.6mm | Mtr | 0 |  |  |  | 0 | 0 | 0
4.8.2 | 300mm x 50mm x1.6mm | Mtr | 0 |  |  |  | 0 | 0 | 0
4.8.3 | 450mm x 75mm x 2.0mm | Mtr |  |  |  |  | 0 | 0 | 0
| Sub Total of 4.0 | [5 empty] | 0 | 0 | 0
5 | LIGHT FIXTURES & CONTROLS:
5.1 | Providing & Installation of lighting fixtures with lamps as per the details below including necessary hardware such as clamps, nuts, bolts, nails screws and suspension rods as required for fixing the fixtures in position as directed by architect / consultant at site.
5.1.1 | TUBE LIGHT | Nos | 12 |  |  |  | 0 | 0 | 0
| Sub Total of 5.0 | [5 empty] | 0 | 0 | 0
6 | EARTHING :
6.1 | S & I of earth pit comprising of specially designed SEE/Ashlok brand Earth Electrode system 3.00 meter long including necessary materials like side fill compound etc. as required with standard brick masonary chamber with hinged cover and watering arrangement model SEE-60/C with SFC-20/Equivalent | Nos | RO
6.2 | S & I of copper /GI earthing wires/strips in following sizes
6.3 | 8 SWG copper bare wire | Mtr |  |  |  |  | 0 | 0 | 0
6.4 | 12 SWG copper bare wire | Mtr |  |  |  |  | 0 | 0 | 0
6.5 | 25mm x 5mm thick GI strip welded & painted green | Mtr | 50 |  |  |  | 0 | 0 | 0
6.6 | S & I of isolated/dedicated earthing / grounding system for computers etc.using insulated green-yellow copper earthing wire laid/fixed bare on wall/ceiling from separately made earth pit to the equipment in following sizes
6.6.1 | 70 Sqmm copper, yellow-green/green insulation | Mtr
6.7 | S & I of Crimp type copper lugs for the above earth
wires in sizes
6.7.1 | 50/70 sqmm | Nos |  |  |  |  | 0 | 0 | 0
6.8 | S & I of Main bus for isolated earth comprising of 300mm x 50 mm x 6mm thick Tinned copper bar fixed on insulated support and having 30 nos of holes and nut bolts studs for clamping the earth leads,all contained in MS/PVC box of size 400mm x 200mm x 60mm deep and having transparent acrylic cover as approved by the consultant | Nos |  |  |  |  | 0 | 0 | 0
| Sub Total of 6.0 | [5 empty] | 0 | 0 | 0
7 | Miscellaneous Item
7.1 | Supply & Install. Of RG 6 TV Cable in existing 25mm PVC Conduit | Mtr. | 0 |  |  |  | 0 | 0 | 0
0
7.2 | Supply & Laying of RG11 use for Main Cable TV | Mtr. | 0 |  |  |  | 0 | 0 | 0
7.3 | Install. Of TV Stand - Only Installation | Nos. | 0 |  |  |  | 0 | 0 | 0
| Sub Total of 7.0 | [5 empty] | 0 | 0 | 0
8 | FIRE DETECTION SYSTEM (ANALOGUE ADDRESSABLE)
Note
The Main Fire Panel shall have 2 way communication. In case of fire signal all the access control doors shall deactivate.
The access control doors will get de activated for people evacuation
Emergency evacuation message will pass through public address system
Dampers will get deactivated through the modules to close the air movement.
Control Module for lift pressurization fans and ventilation fans to be actuated by Main Fire Alarm Panel.
8.1 | Supply, installation, connecting, testing and commissioning of addressable photoelectric type Smoke Detectors (AFC & BFC) with mounting base, blinking LED etc. complete as required. | Nos. | 2 |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.2 | Supply, installation, connecting, testing and commissioning of addressable Type Multi Sensor Smoke Detectors with mounting base etc. complete as required. | Nos. |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.3 | Supply, installation, connecting, testing and commissioning of addressable rate of rise cum fixed temperature Heat Detectors with mounting base, blinking LED etc. complete as required. | Nos. |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.4 | Supply, installation, connecting, testing and commissioning of Addressable Hooters cum strobe min. 80 db output and 110 candelas complete with control modules. The strobes shall be synchronised for better evacuation. | Nos. | 1 |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.5 | Supply, installation, connecting, testing and commissioning of Addressable Manual Call Box in ABS plastic as required complete. | Nos. | 1 |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.6 | Supply, installation, connecting, testing and commissioning of addressable fault Isolator | Nos. |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.7 | Supply, installation, connecting, testing and commissioning of addressable control module for HVAC Panel, Fire damper Electrical panel, PA system & Access Control System | Nos. |  |  |  |  | 0 | 0 | 0
8.9 | Supply, installation, connecting, testing and commissioning of addressable control module for Hooter | Nos. |  |  |  |  | 0 | 0 | 0
8.1 | Supply, installation, connecting, testing and commissioning of addressable monitor module for integration of builder panel to main fire panel | Nos. |  |  |  |  | 0 | 0 | 0
8.11 | Supply, installation, connecting, testing and commissioning of addressable control module for integration of builder panel to main fire panel | Nos. |  |  |  |  | 0 | 0 | 0
8.12 | Supply,installation ,testing and commissioning of Microprocessor based 2 loop panel,Networkable analog addressable type fire alarm control panel with 640 character LCD display.The panel shall equiped with sufficient no. of loops,each loop shall have capacity of 250 analog devices in each loop four access levels,capable of taking flash scan devices,Flash EPROM sufficient no. of programmable relay controls for controlling AHU's,pressurization fans,ventilation fans at fire pump room,monitoring of fire hydrant and fire sprinkler,240v AC power supply,automatic battery charger,24v sealed lead acid battery sufficient for 24hrs normal working and 2hrs during emergency as required according to specification.The panel shall be UL864 9th edition listed with response time less than 10sec.The Panel shall be able to Integrate with BMS & Security System on Common TCP/IP Ethernet Communication Bus using BACnet Transfer protocol.The panel shall have the web enabled facility which can able to send or receive e-mails with memory of 1000 events recording.Note:The vendor shall provide panel UL 9th edition listing certificate. (Make: Edwards / Honeywell / Tyco-Simplex)
| Necessary Integration Facility with BMS for following functions:- | Set |  |  |  |  | 0 | 0 | 0
Alarm, Trouble condition,Supervisory alerts to BMS
Share Graphics of Security, Fire and HVAC
Web Interface
As the number of hooters are 43, additional power supplies to be provided as required.
8.13 | Supply, Installation , Testing and commissioning of Fire Alarm Graphics Software (FAS) as per specifications. The PC will be provided by the IT team. The specifications will be provided by you for the same. | Set | RO
8.14 | Providing and fixing in position 1.2mm thick M.S. rectangular outlet boxes for housing smoke detectors/heat detectors on the true Ceiling complete with all fixing accessories as required | Nos |  |  |  |  | 0 | 0 | 0
8.15 | Supply & laying of following grade with copper conductor armoured FIRE SURVIVAL cable with (EPR) Ethylene Propylene rubber insulation as per IEC-60502:2004 Part-1 (Armoured), Retain circuit integrity as per BS 6387 C.W.Z (armoured), BS 8434-2: 2009 (armoured), (Resistance to fire at 950º C for 3 hours), as per specifications in cable trays, clamped including anchor fastners to wall with suitable clamps, saddles fixing bolts, 2 Nos. of cable glands for each detector back box, complete in all respect as required as per specifications.(Red Colour)
a. | 2 Core x 1.5 sq. mm | RM | 15 |  |  |  | 0 | 0 | 0
| Sub Total of 8.0 | [5 empty] | 0 | 0 | 0
9 | CCTV SYSTEM
9.1 | Supply & Installation of 2 Megapixel IR-20Mtr. IP Indoor Dome Camera (Make: Honeywell / Hikvision) | Nos. | 2 |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.2 | Supply & Installation of 16 Channel NVR with 4 Sata Hard Disk Slot (Make: Honeywell / Hikvision) | Nos. |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.2 | Supply & Installation of 8 Channel NVR with 2 Sata Hard Disk Slot (Make: Honeywell / Hikvision) | Nos. |  |  |  |  | 0 | 0 | 0
9.3 | Supply & Installation of 24Port PoE Switch (Make: Systimax) | Nos. |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.4 | 4 TB HDD Hard Disk | Nos. |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.5 | Supply & Installation of CAT-6 Cable for Camera Signal | Mtr. | 50 |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.6 | Supply and laying of 25mm Dia. PVC Conduit complete with support brackets/clamps, junction boxes etc. complete. | Mtr. | 50 |  |  |  | 0 | 0 | 0
| Sub Total of 9.0 | [5 empty] | 0 | 0 | 0
10 | TELEPHONE AND DATA DISTRIBUTION
11.1 | Supply & laying indoors multipair 0.5mm dia copper PVC insulated and sheathed,armoured/Unarmoured telephone CAT 5 cables on walls, ceiling, cable trays complete with clamps, cable markers etc. from MDF to the various tag blocks as specified
11.1.1 | 10 pair cable armoured Cable | Mtr. | 50 |  |  |  | 0 | 0 | 0
11.2 | Multipair cable end termination including brass glands compression nut, flat check nut soldering of connections on both sides of the tag block 'etc. as specified complete for:
11.2.1 | 10 pair cable armoured Cable | Each | 2 |  |  |  | 0 | 0 | 0
11.3 | Supply & installation of telephone tag block with KRONE terminal connectors, G.I.J.B as specified & complete with all interconnections and jumper connections between the two tag blocks on all floors as shown on drgs.
11.3.1 | 10 pair tel. tag block | Nos. | 1 |  |  |  | 0 | 0 | 0
11.4 | Supply & installation of PVC RIGID conduits with junction boxes, reducer etc. complete concealed/surface mounting as required.
11.4.1 | 25 dia conduit | Mtr. | 50 |  |  |  | 0 | 0 | 0
11.5 | Supply & providing of CAT 6 UTP cables in the already laid raceways / Conduits including terminations | Mtr. | 50 |  |  |  | 0 | 0 | 0
11.6 | Supply & Installation of Single Face Plate. | Nos. | 10 |  |  |  | 0 | 0 | 0
11.7 | Supply & Installation of Dual Face Plate. | Nos. |  |  |  |  | 0 | 0 | 0
11.8 | Supply & Installation of Quadra Face Plate. | Nos. |  |  |  |  | 0 | 0 | 0
11.9 | Supply & Installation of I/O DATA Outlet (RJ-45) | Nos. | 10 |  |  |  | 0 | 0 | 0
11.1 | Supply & Installation of I/O TELEPHONE Outlet (RJ-11) | Nos. | 10 |  |  |  | 0 | 0 | 0
11.11 | Installation of Wi-Fi Access Point | Nos. | 1 |  |  |  | 0 | 0 | 0
| Sub Total of 11.0 | [5 empty] | 0 | 0 | 0