## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
1 | KITCHEN EXHAUST AIR SCRUBBER
Supply, Installation, Testing and Commissioning of Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications.
Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type SS Filters with aluminium mesh filters, Tungsten wire type type ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area, collection area should not be less than 6.0 sqmt, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state and entier unit should be CE Certified. all units shall have shall be equipped with Pulse width modulating (PWM) The system should be fitted with interlock switch for safety. The units should be BMS compatible for Feedback information on Run,Wash and Fault,dry contact point. The system should allow connection to a fan section to achieve velocity between 2.5 - 3.8 m/s across the air cleaner and should units should meet MERV 15 requirements even at velocity of 3.81 m/s (750 FPM)
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
ESP Power Consumption : Not more than 50W per cell.
Air Moving Capacities are as follows:
| 4700 CFM | No. | 1
2 | FAN COIL UNITS
Supplying, installing, testing and commissioning of horizontal powder coated Medium Static Chilled Water Fan Coil Units, blow thru type, Noscomplete with 3/4 rows deep chilled water coil, one or more centrifugal fans, aluminum/synthetic cleanable pre-filters,Digital thermostat with necessary control and power wiring with PVC conduit etc. type , primary inside pan SS-304 & secondary condensate drain pans outside of GI duly insulated, casing, coil, piping connections through copper pipes, condensate drain connection, All fan coil units shall be suitable for 220±6% volts, 50 cycles single phase power supply. All fan coils shall be with factory fitted with complete valve station, 2 way PIBC chilled water valve along with On -off type 220/230 volt AC actuator , brass made Y strainer type ball valve, brass ball valve.All valves shall be of minimum PN-16 pressure rating Quoted rates shall be inclusive of the cost of valve's thermal insulation (CFC & HCFC free) as specified for chilled water piping thermal insulation, 2 way PIBC Motorized Valves provided with spring return function in chilled water lines at Nosfan coil unit. The valves shall be suitable for suitable pipe sizes. 2 way PIBC control valve chilled water valve will be of PN16 rating complete with motor 220/230 volt AC of actuator of suitable torque.The valve should be IEC 534 compliant , have 20 mm stroke All shall be supplied as per tender specifications and data sheet. Fan coil unit shall be of following arrangement and refrigeration capacity.Control wiring from thermosets to FCU motor & PICV valve unto 20 Mtr. length shall be inclusive. 3C x 1.5 Sq.mm.Power cable of 3 mtr.length with 3 pin plug top from unit motor to the nearest power socket shall be included in the scope of supply.All supporting GI hangers, ,MS angles, channels nut , bolts, washers etc. necessary for unit installation shall be inclusive in the cost. Unit should supply with necessary Corded Remote Controller.
| 2.5 TR ( 1000 cfm) | Nos. | 1
3 | Ceiling Suspended AHU
Supplying, installing, testing and commissioning of double skin construction draw thru type Ceiling Suspended AIR HANDLING UNITS as per specification, each complete with ESP Filter (94% down to 3 microns), pre-filter section (90% down to 10 microns), min 6 Row Deep Chilled water coil of copper tube & aluminium fins construction, squirrel cage induction motor, airfoil centrifugal fan belt drive and vibration isolators, coil size shall be selected for a maximum face velocity of 500 feet/minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (IE2) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Fan motor assembly (as whole) shall be statically and dynamically balanced to grade G 6.3 as per ISO-1940/AMCA 204-3.All units shall be complete with opposed blade volume control dampers at oulet. Duct flexible connector (fire proof) shall be provided at outlets of AHU. ( Temporary bypass arrangement in Chilled Water Line with related accessories to be considered to facilitate flushing during precommissioning and commissioning of the System).
AHU Tag. Description AHU CFM TR ESP Motor HP
| AHU-01 Sitting area 3000 cfm 6 15 mm 2 | No. | 1
4 | Supplying, installing, testing and commissioning of AIR HANDLING UNITS ( FAN SECTIONS ONLY)with double skin construction as per specificatopns, each complete with squirrel cage induction motor (mounted internally), airfoil centrifugal fan belt drive and vibrations isolators.Motors shall be suitable for 415 +- 10% volts, 50 cycles , 3 phase AC supply an static pressure shall be as indicated . Fan-motor assembly (as whole) shall be statically & dynamically balanced to grade G6.3 as per ISO-1940/AMCA 204-3. AHUS (Fan sections) shall be complete with duct flexible connections and volume control damper . In additional all supply fans (SF) shall be provided with prefilter
SF - Supply Fan
Sr.no Fan Tag Space Fed CFM SP Motor HP (mmwg)
| 1 SF -01 Kitchen 4250 40 3 | No. | 1
5 | Supply, installation, testing and commissioning of single width single inlet class I centrifugal fans for ventilation system. Each fan shall be complete with totally enclosed fan cooled motor, belt drive, pulley mounted on motor & fan shaft, belt guard, motor mount and vibration isolators. The motor shall be suitable for 415 V + 10% volts 3 phase 50 cycles, AC supply & suitable for operating through VFD. The motor selected shall be energy efficient having efficiency at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. The fan shall be low RPM and capacities based on 2.5 inch (6.5 cm WC) static pressure. Fan capacities shall be as follows:
EF - Exhaust Fan
Sr.no Fan Tag Space Fed CFM SP Motor HP (mmwg)
| 1 EF -01 Kitchen 4700 65 5 | No. | 1
6 | Ductable Split unit
Supply, installation, testing and commissioning of CONCEALED Duct type units with Scroll compressor with green Regrigerant R-410A/R-32/R-22. The unit should be complete with indoor & outdoor unit, condensing unit, controls, control panel, tubular type refrigerant, canvas connection remote control and drain piping. The refrigerant piping, control wiring should be based on the indoor unit and outdoor unit distance being 3 mtrs/Ckt along with 13 mm thk nitrile rubber insulation. The insulated drain piping should be of 32 mm dia. and distance 3 mtrs/unit. Indoor unit should be provided with thermostats and remote control. The installation should be complete with all the required accessories like the supports, clamps required to make the installation complete. The cost should also include Chasing in walls as well as all the supports needed to install the units at the higher level.
The quoted price shall include the GI frame structure to mount the outdoor unit or to suit the site condition.
6.1 | 8.5 TR ( 3400 cfm) HSP split air conditioning units as described above | No. | 1