## Electrical
ELECTRICAL BOQ
WBS | Short Text | Description | UOM | Qty | Unit Price | Remarks
SECTION - I - POWER & LIGHTING POINTS
1.1 |  | Supply and Installation of all materials, accessories and labour for point wiring for power or light or equipment circuit main using PVC insulated stranded copper conductor FRLS wires of 650V grade drawn through Rigit Metal MS Conduit along with switch boards.Flex conduit to be used for turning.(The cost of the conduit will be taken with point wiring) using necessary conduit accessories,junction boxes, etc. The rate shall include the cost of providing PVC insulated stranded copper conductor earth wire in each conduit alongwith other circuit main wires. Lugs to be use at both the ends. FRLS wiresType only.Primary point of power point should be considered upto 20 Mtr & Light point should be considered upto 15MTR wire & all secondary points upto 5 Mtr.Above rate should include all wires,conduits,support,hardwate & other required all accessories,scaffolding etc. Work to be completed in all respect. NO ADDITIONAL CIRCUIT LENGTH WOULD BE PROVIDED FOR ANY POWER OR LIGHTING POINT. MEASUREMENT WILL BE TAKEN ON THE PURE COUNT OF NOS OF POWER & LIGHT POINTS
1.1.1 |  | Primary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Power point cost to be included with back box,Switches,Socket,Modulat plate all inclusive. FOH area plates to be black & Kitchen SB to have white color switch board. (For Equipments/Computers/Convenience points) | Nos. | 53
1.1.2 |  | Secondary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire.Power point cost to be included with back box,Switches,Socket,Modulat plate all inclusive. FOH area plates to be black & Kitchen SB to have white color switch board. (For Equipments/Computers/Convenience points) | Nos. | 35
1.1.3 |  | Primary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Lighting wiring min conduit size to be 20mm. 20mm conduit should not have maximum 2 or 3 circuit. All conduits should not be full with 3 circuit. Future provision space to be left in some conduits. Juction boxes,Ceiling rose,connector for light fixture to be installed. (Lights directly controlled from distribution board) | Nos. | 25
1.1.4 |  | Secondary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Lighting wiring min conduit size to be 20mm. 20mm conduit should not have maximum 2 or 3 circuit. All conduits should not be full with 3 circuit. Future provision space to be left in some conduits.Juction boxes,Ceiling rose,connector for light fixture to be installed. (Lights directly controlled from distribution board) | Nos. | 105
1.1.5 |  | Primary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Lighting wiring min conduit size to be 20mm. 20mm conduit should not have maximum 2 or 3 circuit. All conduits should not be full with 3 circuit. Future provision space to be left in some conduits.Juction boxes,Ceiling rose,connector for light fixture to be installed.Avg circuit 15 Mtr (Lights controlled from individual switch board) | Nos. | 5
1.1.6 |  | Secondary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Lighting wiring min conduit size to be 20mm. 20mm conduit should not have maximum 2 or 3 circuit. All conduits should not be full with 3 circuit. Future provision space to be left in some conduits.Juction boxes,Ceiling rose,connector for light fixture to be installed.Avg Length 7 Mtr (Lights controlled from individual switch board) | Nos. | 3
1.2 |  | Supplying and installing all materials, accessories and labour for conduiting & the accessories for light/ Equipment circuit main.The conduit should be Medium gauge rigid 1.6 mm thick GI conduits conforming to IS-2509 of 1973 . The conduits shall be clamped by GI saddles . The clamps/supports shall be fixed to the underside of the ceiling or floor by means of nylon rawl plugs and brass screws of 3 mm size. Anchor fasteners of suitable sizes shall be provided if necessary. The conduits shall be supported at regular intervals of 500 mm. Additional supports shall be provided on either side of bends, JB's & terminations. The conduits shall be bent with bending springs to provide smooth bends. Use of ready made bends shall be kept to a minimum. The jointing of GI conduits shall be done with couplers. Conduits to be terminated in GI Boxes shall be terminated with female adaptors with bushes. End portion of the conduit to be provided with end caps where ever necessary. The cost should include the cost of heavy gauge rigid GI conduit with necessary conduit accessories, GI pull/junction boxes, GI fish wire etc & laying of the same. FRLS Only
1.2.1 |  | 25mm PVC Conduit | Rmt | 60
1.2.2 |  | 32mm PVC Conduit | Rmt | RO
1.2.3 |  | 75X45mm Aluminium Rectangle tube Raceway | Rmt | RO
1.2.4 |  | 80X60mm Aluminium Rectangle tube Raceway | Rmt | RO
1.3 |  | Supply & installations of GI Powder coated, Junction Boxes made of 2.0 mm thk/1.6mm thk, with removal GI Powder coated Top Cover 2.0mm thk, all side entries for raceways, complete with all accessories. The rate to include fixing the juncrtion box on the floor Trenches or floor described above. Sample junction box to be approved first.
1.3.1 |  | 150mm x 150mm GI Junction Box | Nos. | R0
1.3.2 |  | 200mm x 200mm GI Junction Box | Nos. | R0
1.3.3 |  | 300mm x 300mm GI Junction Box | Nos. | R0
SECTION-II-SUPPLY & INSTALLATION OF WHETHER PROOF SWITCH SOCKET OUTLETS
2.2 |  | Supply & Installation of switches, sockets, complete with MS boxes & front plate inter - connections, box earthing & its complete accessories.Wiring to be included switch board. Avg length of Primaty point upto 20 Mtr & Secondary point upto 8 Mtr. All wiring to be complete with all accessories. Conduit to be used as Rigid Metal.
2.2.1 |  | Primary Point - 6/16A Switch Socket Outlet (RAW Power) - Whether Proof for outside | Nos.
2.2.2 |  | Secondary Point - 6/16A Switch Socket Outlet (RAW Power) - Whether Proof for outside | Nos.
SECTION III-TELEPHONE / DATA SYSTEM AND TV
3.1 |  | Supply & Installation of the Cat6 information outlet with face plate. (For data). | Nos. | 30
3.2 |  | Supply & Installation of Cat. 6 Data cable via 20/25mm Metal Conduits with tagging & ferruling & crimping at both the ends. | Rmt | 1450
3.3 |  | Supply & Installation of RJ11 telephone outlet with plate and box | Nos | RO
3.4 |  | Supply & Installation of CAT5 cable in 20/25mm dia GI conduit for telephone | Rmt | RO
3.5 |  | Supply & Installation of 20 pair telephone tag block with enclosure | Nos | 0
3.6 |  | TV out let socket with white face plate & Metal back box | Nos | 0
3.7 |  | 4W / 6W Splitter fot TV cables | Nos | 0
3.8 |  | Supply, installation of RG59/RG6 Co-axial cable for TV with PVC Conduits 25mm/32 mm fixed to walls/Ceiling with Spacers & saddles or taken through false ceiling or raceways | Rmt | 0
SECTION IV-LIGHTING
4.1 |  | Installation of the following light fittings (Light Fixtures will be supplied by Client)
4.1.1 |  | Suspended Linear | Nos
4.1.2 |  | Suspended Chandelier | Nos | 37
4.1.3 |  | Surface Mounted or Concealed Downlight/Downlight | Nos | 65
4.1.4 |  | Covelight | Rmt | 25
4.1.5 |  | Supplying, installing, testing and commissioning of suitable size of dimmer panel for 10 Nos. circuit with 6 to 8 Nos light fixture on each circuit 2000W light load, complete as required . (Make-Wipro/ABB) | Nos | 1
SECTION-V PANELS, DISTRIBUTION BOARDS
5.1 |  | Supply,Installation, Testing & Commissioning of Floor/Wall mounted cubicle type LT panel/DB of CRCA sheet steel (2mm Thickness) construction with total front access for switchgear and top entry for all incoming and outgoing cables. Totally compartmentalized including proper Al/Copper bus bar chambers, cable alley, etc. as per SLD. 160A - MCCB Incomer ELR - 300 MA O/V Voltage Relay Single Phase Preventor Al Bus Bar - 200A Earthing strip - 2 Nos Cooling Fan - APFC Section APFC - 28 to 30 KVAR Out going feeder as per SLD with RCBO Inbuit 14WAY SPN LDB 1 Inbuit - 12WAY TPN RPDB Phase Lamp Emergency Stop Botton All AHU Starter panel with VFD Floor Standing Panel Tube type Fire Suppression system | Nos | 1
5.1.1 |  | 8 Way ETPN (LDB-2) with 1 no 40A FP RCBO 100mA as incomer and 24 nos of 6/10/16A MCB as Outgoings (RAW DB) | Nos. | 1
5.1.2 |  | 12 Way ETPN (LPDB) with 1 no 63A FP RCBO 100mA as incomer and 24 nos of 16A MCB as Outgoings (Raw Power) | Nos.
5.1.3 |  | 16 Way SPN (UPSDB1) with 1 no 63A DP RCBO 100mA as incomer and 14 nos of 6/10/16A MCB as Outgoings | Nos. | 1
5.1.3 |  | 12 Way SPN (UPSDB2) with 1 no 25A DP RCBO 100mA as incomer and 8 nos of 6/10/16A MCB as Outgoings | Nos. | 1
SECTION-VI -CABLING & EARTHING
6.1 |  | Supply of Installation of Following cables 1.1 KV grade PVC/XLPE insulated Armoured Aluminium/Copper conductor cables. The cables shall be laid as per dwgs or on cable trays laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with earthing as specified for continuous earthing along with cable . (The cost of the cable trays or ladders, excavation and back filling of trenches will be measured separate. The unit cost of the cable shall include clamps, fasteners etc. as required for proper installation. Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by consultant/site engineer. The cables should be properly dressed and to be tied to the cable trays using appropriate cable ties.
a |  | 2 C X 2.5 sq. mm. CU ARMOURED | Rmt
b |  | 3.5 C X 50 sq. mm. CU ARMOURED | Rmt
c |  | 3.5 C X 70 sq. mm. CU ARMOURED | Rmt
d |  | 3.5 C X 95 sq. mm. CU ARMOURED | Rmt
e |  | 3 C X 2.5 sq. mm. CU PVC ARMOURED | Rmt | 25
f |  | 3 C X 4 sq. mm. CU PVC ARMOURED | Rmt | 15
g |  | 3 C X 6 sq. mm. CU PVC ARMOURED | Rmt | 60
h |  | 3 C X 10 sq. mm. CU PVC ARMOURED | Rmt
i |  | 3 C X 16 sq. mm. CU PVC ARMOURED | Rmt
j |  | 4 C X 16 sq. mm. CU PVC ARMOURED | Rmt
k |  | 4 C X 2.5 sq. mm. CU PVC ARMOURED | Rmt
l |  | 4 C X 4 sq. mm. CU PVC ARMOURED | Rmt | 210
m |  | 4 C X 6 sq. mm. CU PVC ARMOURED | Rmt | 80
n |  | 4 C X 10 sq. mm. CU PVC ARMOURED | Rmt | 50
o |  | 4 C X 16 sq. mm. AL. PVC ARMOURED | Rmt | 40
p |  | 4 C X 25 sq. mm. AL. PVC ARMOURED | Rmt
q |  | 4 C X 35 sq. mm. AL. PVC ARMOURED | Rmt
r |  | 3.5 C X 50 sq. mm. AL. XLPE ARMOURED | Rmt
s |  | 3.5 C X 70 sq. mm. AL. XLPE ARMOURED | Rmt
t |  | 3.5 C X 95 sq. mm. AL. XLPE ARMOURED | Rmt
u |  | 3.5 C X120 sq. mm. AL. XLPE CABLE ARMOURED | Rmt
v |  | 3.5 C X185 sq. mm. AL. XLPE CABLE ARMOURED | Rmt
6.2 |  | Supply of Installation of Following cable Terminations including Single/Double compression type chrome plated brass glands and lugs(crimping type), PVC taping as required and all accessories complete.
a |  | 2 C X 2.5 sq. mm. CU ARMOURED | Nos
b |  | 3.5 C X 50 sq. mm. CU ARMOURED | Nos
c |  | 3.5 C X 70 sq. mm. CU ARMOURED | Nos
d |  | 3.5 C X 95 sq. mm. CU ARMOURED | Nos
e |  | 3 C X 2.5 sq. mm. CU PVC ARMOURED | Nos | 2
f |  | 3 C X 4 sq. mm. CU PVC ARMOURED | Nos | 2
g |  | 3 C X 6 sq. mm. CU PVC ARMOURED | Nos | 4
h |  | 3 C X 10 sq. mm. CU PVC ARMOURED | Nos
i |  | 3 C X 16 sq. mm. CU PVC ARMOURED | Nos
j |  | 4 C X 16 sq. mm. CU PVC ARMOURED | Nos
k |  | 4 C X 2.5 sq. mm. CU PVC ARMOURED | Nos
l |  | 4 C X 4 sq. mm. CU PVC ARMOURED | Nos | 12
m |  | 4 C X 6 sq. mm. CU PVC ARMOURED | Nos | 4
n |  | 4 C X 10 sq. mm. CU PVC ARMOURED | Nos | 2
o |  | 4 C X 16 sq. mm. AL. XLPE ARMOURED | Nos | 2
p |  | 4 C X 25 sq. mm. AL. XLPE ARMOURED | Nos
q |  | 4 C X 35 sq. mm. AL. XLPE ARMOURED | Nos
r |  | 3.5 C X 50 sq. mm. AL. XLPE ARMOURED | Nos
s |  | 3.5 C X 70 sq. mm. AL. XLPE ARMOURED | Nos
t |  | 3.5 C X 95 sq. mm. AL. XLPE ARMOURED | Nos
u |  | 3.5 C X120 sq. mm. AL. XLPE CABLE ARMOURED | Nos
v |  | 3.5 C X185 sq. mm. AL. XLPE CABLE ARMOURED | Nos
w |  | 3.5 C X400 sq. mm. AL. XLPE CABLE ARMOURED | Nos
6.3 |  | Supply & Installation of Following Cable Trays of 2mm thick GI fabricated ladder type cable trays of the following sizes. Ladder type cable trays shall be fabricated from 50 x 50 x 5 mm GI angles on the sides with 25 x 6 mm GI strips welded at intervals of 300 mm. The trays shall be painted with 2 coats of red oxide & 2 coats of synthetic enamel paint of approved colour. All trays should have coupler plates with 4 number of bolt and nuts of galvanized hardware.Trays should be supported at ecvery 1.5 mtr interval.
6.3.1 |  | 200mm wide perforated cable tray with support (Power Supply) | Rmt | 10
6.3.2 |  | 300mm wide perforated cable tray with support (LV supply) | Rmt | 25
6.4 |  | Supply & Installation of Chemical Earthing station as per specification and IS: 3043-1985 for equipment earthing for panel and equipment earthing. Following guidelines to be maintained: | Nos.
Excavation in hard marrum
Chemical compound
Earthing strip / Earthing cable
Cu pipe in pipe electrode
Hardware
Brick masonry chamber with C.I. hinged cover and funnel
Equipotential bar
6.5 |  | SITC of earthing wire including necessary accessories, clamped on over head slab or walls, laid over false ceiling or in wall chases. Rate to include making good the wall chases with cement mortar. Interconnection between lengths should be as per specifications and as per good installation practice.
6.5.1 |  | 10 SWG GI Wire | Rmt | 420
6.5.2 |  | 25 X 3 mm GI Strip | Rmt | 10
6.5.3 |  | 1 core x 6 sq.mm .Cu wire | Rmt | 75
6.5.4 |  | 1 Core x 2.5 Sq.mm Cu Wire | Rmt
SECTION-VII -IP SYSTEM CCTV
7.1 |  | SITC 3+1 CCTV flexible cable in 20/25mm Metal MS conduit | Rmt | 650
7.2 |  | SITC RG6 co-axial cable in 20/25mm Metal MS conduit (For CCTV and LED TV) | Rmt
7.3 |  | SITC H.264 standalone DVR, 8 ch video, cif real-time, d1 non real-time, 1 sata hdd 2 tb cp-plus 0804hxt | Nos
7.4 |  | SITC IP color indoor IR dome camera: GE est 12vdc, 24 ir led, , fixed board lens f=3.6mm ceiling mounted | Nos
7.5 |  | SITC Power supply 12v dc protek pktps1012nabs | Nos
7.6 |  | SITC 18.5" (19") TFT monitor with wall mount bracket Samsung b1930 | Nos
7.7 |  | SITC of Cat 6 cctv cabling in Metal MS Conduit | Rmt
SECTION-VIII -UPS
SITC of 1 phase online UPS for all critical load. Computer load & IT load will be on separate UPS . Separate DB to be planned of UPS. UPS load to be balance in all phase.Battery bank to ne planned seperately on MS rack.UPS to connected with i/O MCB boxes.30 min should min backup on full load condition.
8.1 |  | 6KVA | Nos. | 1
8.2 |  | 3 KVA | Nos.
8.3 |  | Providing Temprory Light Fixture | job | 1
8.4 |  | Removing of Existing Cables Wiring, Conduits, Light Fixture,Fire Equipments and related Itmes | job
SECTION-IX-GAS DETECTION SYSTEM
9.1 |  | SITC of FR 4C x 1.5 sq. mm 1100V copper conducter, PVC insulated cable and shielded armoured and PVC sheathed cable for Gas Detection System. Cable shall be cleated to wall and ceiling (Red colour) | Rmt | 130
9.2 |  | SITC of Gas panel & LED lamp indicator in case of detection. | Nos | 1
9.3 |  | SITC of gas detector to be mounted at gas flexible hose | Nos | 2
SECTION-X-MUSIC SYSTEM
10.1 |  | SITC of 70/36 Transparent Speaker cable in 20/25mm MS metal conduit | Rmt | 225
10.2 |  | SITC of 15W speakers SPW4 to be mounted on ceiling / Wall | Nos
10.3 |  | SITC of Sub-woofer SPW8S to be mounted on ceiling. | Nos
10.4 |  | SITC of 15W speakers SPW4 to be mounted on wall. | Nos
10.5 |  | SITC of Sub-woofer SPW8S to be mounted on wall. | Nos
10.6 |  | SITC of get up signaling device. | Nos
10.7 |  | Installation of amplifier 120W for music system suitable to operate on 230V AC/12V DC, with low impedance microphone input & two auxiliary inputs, tone control, protection circuit complete for the speakers output 4/8/16 lines | Nos
10.8 |  | SITC of table top microphone | Nos
SIEMENS /L&T MAKE MK1 3 PHASE DOL STARTER FOR ALL EXHAUST FAN/FRESH AIR/INLINE FAN
10.9 |  | 7.5 KW | Nos.
10.1 |  | 5.5 KW | Nos.
10.11 |  | 3.7 KW | Nos.
10.12 |  | 2.2 KW | Nos.
10.13 |  | Above 7.5KW Star/Delta Starter (3 Phase)
SITC OF ENCLOSURES FOR MCB FOR OUTDOOR APPLICATION WITH MCB DP & FP
10.14 |  | DP MCB in weather proof enclosure with MCB
a |  | 40-63A | Nos
b |  | 6-32A | Nos | 2
10.15 |  | TPN MCB in weather proof enclosure with MCB
a |  | 80-100A | Nos
b |  | 40-63A | Nos | 5
c |  | 6-32A | Nos
10.16 |  | SITC OF INDUSTRIAL TYPE METRA PLUG/TEMPRA PLUG FOR EQUIPMENT POWER CONNECTIONS WITH REQUIRED MCB
a |  | 63A 5Pin 3 Phase Plug and Socket with TPN MCB | Nos | 1
b |  | 40A 5Pin 3 Phase Plug and Socket with TPN MCB | Nos | 1
c |  | 20/32A 3Pin Single Phase Plug and Socket with DP MCB | Nos | 5
d |  | 20A 2Pin SP Metal Clad Socket with SP MCB (Industrial Type) | Nos
SECTION-XI- IT (Passive)
11.1 |  | CAT 6 -305 M | Nos
11.2 |  | Jackpanel | Nos
11.3 |  | CAT 6 IO | Nos
11.4 |  | 4 port wall plate | Nos
11.5 |  | 2 port Wall plate | Nos
11.6 |  | Patch cables - 2mtrs | Nos | 20
11.7 |  | Patch cables - 1mtrs | Nos | 20
11.8 |  | Cable laying & IO Punching , Face plate installation,crimping ,testing ,Rack dressing,
SECTION-XII- FIRE ALARM SYSTEM
1 |  | SITC of wall mounted 1 zone addressable type fire panel & same to be intergrated with building BMS system. FAS panel to be UL/FM listed. Make- Notifier (Honeywell)
|  | Fire panel to also give output to trip HVAC system. | Nos. | 1
2 |  | SITC of 2C x 1.5 Sq.mm, 1100V copper conductor, PVC insulated and sheilded armoured and overall FRLS PVC sheathed red color cable for fire Alarm system. Cable shall be cleated to wall, ceiling with required accessoires all complete. | Rmt | 350
3 |  | SITC of Smoke detector addresable type | Nos. | 18
4 |  | Response Indicator for smoke Detector | Nos | 7
5 |  | SITC of Heat detector | Nos | 3
6 |  | SITC of MCP at all exit door | Nos. | 3
7 |  | SITC of Hooter | Nos. | 3
8 |  | SITC of repeater module for integration with mall system | Nos | 1
SECTION-XIII- FIRE EXTINGUISHER
SITC of Fire Extinguisher with cylinder & it’s wall mounted brack & floor stand as per site condition. Signage to be pasted on wall at the location of Fire Extinguisher
1 |  | ABC Type- 5 Kg | Nos | 8
2 |  | CO2 Type - 5 Kg | Nos | 1
3 |  | K Type - 5 Kg | Nos | 1
4 |  | ARFF Type - 5 Kg | Nos | 1
TOTAL
GST @ 18%
GRAND TOTAL