## Plumbing & Sprinkler Works
WBS | Short Text | Description | UOM | Qty | Unit Price | Remarks
1 |  | Providing , laying and jointing best quality rigid SCH 40 - uPVC pipes ( Astral, Prince or Supreme make) with all fittings etc. for waste drains from wash basin, sinks, etc. or vent connections from sanitary fittings to vent pipe including testing etc. complete with screwed points, Rates inclusive of floor traps, floor extension piece, drain points, etc Complete
|  | 160 mm OD - | Rm
|  | 110 mm OD - | Rm | 20
|  | 90 mm OD - | Rm
|  | 75 mm OD - | Rm | 25
|  | 50 mm OD - | Rm | 15
|  | 40 mm OD - | Rm
|  | 32 mm OD - | Rm
|  | 25 mm OD - | Rm
|  | 20 mm OD - | Rm
|  | 15 mm OD - | Rm
2 |  | Providing , laying and jointing best quality rigid Class 1, SDR 11 CPVC pipes ( Prince / Astral or Supreme make) with all fittings etc. for all sinks, etc. or vent connections from sanitary fittings to vent pipe including testing etc. complete with screwed points. Note: Rates inclusive of All copper based bends, Elbows, and other required fittings
|  | 50 mm OD - | Rm
|  | 40 mm OD - | Rm
|  | 32 mm OD - | Rm | 35
|  | 25 mm OD - | Rm | 70
|  | 20 mm OD - | Rm | 115
|  | 15 mm OD - | Rm
3 |  | Providing and fixing Zolto make Gate /ball Valve with all fittings including Teflon tape and necessary accessories etc.
|  | 50 mm OD - | No.
|  | 40 mm OD - | No.
|  | 32 mm OD - | No. | 2
|  | 25 mm OD - | No. | 5
|  | 20 mm OD - | No. | 30
15 mm OD -
4 |  | Providing and fixing insulation to hot water piping with extended synthetic rubber polymeric compound 9 mm thick preformed pipe sleeves, using propriety adhesive and self adhesive tapes, all as per the manufacturer's specifications.
|  | 15 mm dia | Rm
|  | 20 mm dia | Rm | 40
|  | 25 mm dia | Rm | 10
5 |  | Providing and fixing of following items of approved make including all accessarories and warrantty as per manufacturers specification etc. complete .( As Specified in FF&E Docket/Drawings)
|  | Long Body Bib Cock (Jaguar:CON-347KNM) | No. | 4
|  | Wall Mixer (Jaguar:CON-309KNM) | No. | 2
|  | Deck Mixer (FLR-5167NB) | No. | 2
|  | Angle Cock (Jaguar:CON-053KN) | No. | 30
|  | Basin Faucet (Jaguar:FLR-5231K) | No. | 1
|  | Bar Sink Cock (Jaguar:FLR-5357N) | No. | 3
|  | Pre rinse Hand Shower(ONLY FITTING) | No. | 1
|  | Sensor Tap(ONLY FITTING) | No. | 1
|  | Connection Pipe | No. | 30
|  | Wash Basins as per Design | No. | 1
|  | Waste coupling | No. | 1
|  | bottle trap | No. | 1
|  | Tissue paper holder ( ONLY FITTING) | No.
|  | Water meter (bill to be submitted) | No. | 1
|  | Soap Dispenser ( ONLY FITTING) | No. | 2
|  | geyser 25litres | No. | 1
|  | geyser 15litres | No.
|  | geyser 10litres | No.
|  | geyser 3litres | No. | 2
|  | 4" x 4" Cockroach Jali with Grating | No. | 8
|  | Bar Sink-Frankie( Only Installation) | No. | 1
|  | Knee operated Sink( Only Installation) | No. | 1
|  | Chicken Inlet Table with Grease Trap( Only Installation) | No. | 1
|  | 2 bowl Veg Prep Sink (Only Installation) | No. | 1
|  | 2 bowl Dish wash Sink with Grease Trap( only Installation) | No. | 1
|  | MOP+ Hand Wash Sink ( Only Installation) | No. | 1
|  | Pot Sink With Grease Trap ( Only Installation) | No. | 1
|  | BOOSTER PUMP(Supply & Installation) | No. | 1
|  | Exit Jaali at End Point | No. | 1
|  | Water tank 1000 litres | No.
|  | Water tank 2000 litres | No. | 1
|  | Submersible Pump/Water Pump | No.
|  | SS 304 Graiters 300*300mm | No. | 8
|  | SS 304 Graiters 300*300mm (Solid Top Cover) | No. | 1
|  | SS 304 Graiters 600*600mm | No.
|  | SS 304 Graiters 900*900mm | No.
|  | Supply & Installation of UPVC Nanhi trap of 4 way type to connect equipment drain. Installation to be completed with all required accessories | No. | 8
PLUMBING WORKS TOTAL
1 |  | SPRINKLER SYSTEM
Pipes : JINDAL
Sprinklers: Tyco/HD/SAFEX
Motor-Kirloskar/Lubi
1.1 |  | Providing, laying, jointing, testing and commissioning pipework for Sprinkler System including including making connection with existing pipework, fixing of pipework on walls, beams, slabs, columns etc. with M.S. supports (duly painted), adjustable ha Material: M.S pipe Class 'C' conforming to IS:1239 for pipes up to 150mm dia. and IS:3589-1991 for pipes above 150mm dia. Fittings: M.S Forged Fittings Up to 50mm dia pipes suitable for threaded/weldable socketed joints ; Heavy Class MS fittings for pipes above 50mm dia. suitable for butt welding and flanged joints. Painting: Pipework shall be painting with two coats of enamel paint of fire red shade over a coat of primer. Piping network to be completed with leakage test with min 14kg water pressure.
a |  | 100 mm dia pipe | Rm
b |  | 80 mm dia pipe | Rm | 10
c |  | 65 mm dia pipe | Rm | 13
d |  | 50 mm dia pipe | Rm | 10
e |  | 40 mm dia pipe | Rm | 15
f |  | 32 mm dia pipe | Rm | 20
g |  | 25 mm dia pipe | Rm | 55
1.2 |  | Providing and fixing of brass body quartzoide bulb type automatic sprinkler heads set to operate at specified temperature of following types. Sprinkler heads shall be complete with deflector.( UL Listed and FM Approved)
a |  | Type : Standard Response Type Pendent Sprinklers Size : 15 mm dia Finish: Chrome Operating Temp. : 68 deg.C. K Factor : 80 | No | 28
b |  | Type : Standard Response Type Pendent Sprinklers Size : 15 mm dia Finish: Chrome Operating Temp. : 141 deg.C. ( for Exhaust Duct) K Factor : 80 | No
c |  | Type : Standard Response Type Pendent Sprinklers Size : 15 mm dia Finish: Chrome Operating Temp. : 93 deg.C. ( for Exhaust Duct) K Factor : 81 | No
d |  | Type : Standard Response Type Upright Sprinklers Size : 15 mm dia Finish: Chrome Operating Temp. : 68 deg.C. K Factor : 80 | No | 15
1.3 |  | Providing and fixing following type of surface rosette for sprinklers, of approved make. ( UL Listed and FM Approved)
Captive rosette
a |  | for 15 mm dia |  | 28
1.4 |  | Providing and fixing 1.2 metre long braided stainless steel (grade AISI 304) flexible tubing suitable for fire sprinkler installation having 1" NPT mail thread inlet and 1/2" NPT female thread outlet. The unit shall be complete with bracket assembly for s | No | 16
1.5 |  | Providing and fixing electric flow switch, capable of sensing a minimum of flow of one sprinkler, including making electrical cable termination.
a |  | For 80 mm dia sprinkler line | No | 1
1.6 |  | Providing and fixing of nickel plated brass/ nonferrous alloy fully way ball valve ( minimum working pressure of 20 bar ) with operating handle of approved make. (Drain Valve)
a |  | 25 mm dia. | No | 1
b |  | 40 mm dia. | No
1.7 |  | Providing and fixing Cast Iron butterfly valve as per IS: 13095 of Class PN 16, having epoxy coated disc, carbon steel shaft, EPDM rubber body liner and of approved make. including a set of MS flanges, required nos. of nut & bolts all complete.
a |  | 100 mm dia with lever | No
b |  | 80 mm dia with lever | No | 1
1.8 |  | Dismentalling of following sizes existing sprinkler pipework including sprinkler heads as per site requirement including disconnecting, pluging,of pipes, upright/pendent sprinklers, fittings etc. (as per site Engineer). complete in all respect The mate
a |  | 150 mm dia pipe | Rm
b |  | 100 mm dia pipe | Rm
c |  | 80 mm dia pipe | Rm
d |  | 65 mm dia pipe | Rm
e |  | 50 mm dia pipe | Rm
f |  | 40 mm dia pipe | Rm
g |  | 32 mm dia pipe | Rm
h |  | 25 mm dia pipe | Rm
1.9 |  | Providing & Tamper switch on main butter fly valve | Nos
SPRINKLER WORKS TOTAL
TOTAL
ADD GST 18%
GRAND TOTAL