## Sheet1
SPRINKLER SYSTEM
Pipes : JINDAL
Sprinklers: Tyco/HD/SAFEX
Motor-Kirloskar/Lubi
Providing, laying, jointing, testing and commissioning pipework for Sprinkler System including including making connection with existing pipework, fixing of pipework on walls, beams, slabs, columns etc. with M.S. supports (duly painted), adjustable ha Material: M.S pipe Class 'C' conforming to IS:1239 for pipes up to 150mm dia. and IS:3589-1991 for pipes above 150mm dia. Fittings: M.S Forged Fittings Up to 50mm dia pipes suitable for threaded/weldable socketed joints ; Heavy Class MS fittings for pipes above 50mm dia. suitable for butt welding and flanged joints. Painting: Pipework shall be painting with two coats of enamel paint of fire red shade over a coat of primer. Piping network to be completed with leakage test with min 14kg water pressure.
100 mm dia pipe | Rm
80 mm dia pipe | Rm | 10
65 mm dia pipe | Rm | 13
50 mm dia pipe | Rm | 10
40 mm dia pipe | Rm | 15
32 mm dia pipe | Rm | 20
25 mm dia pipe | Rm | 55
Providing and fixing of brass body quartzoide bulb type automatic sprinkler heads set to operate at specified temperature of following types. Sprinkler heads shall be complete with deflector.( UL Listed and FM Approved)
Type : Standard Response Type Pendent Sprinklers Size : 15 mm dia Finish: Chrome Operating Temp. : 68 deg.C. K Factor : 80 | No | 28
Type : Standard Response Type Pendent Sprinklers Size : 15 mm dia Finish: Chrome Operating Temp. : 141 deg.C. ( for Exhaust Duct) K Factor : 80 | No
Type : Standard Response Type Pendent Sprinklers Size : 15 mm dia Finish: Chrome Operating Temp. : 93 deg.C. ( for Exhaust Duct) K Factor : 81 | No
Type : Standard Response Type Upright Sprinklers Size : 15 mm dia Finish: Chrome Operating Temp. : 68 deg.C. K Factor : 80 | No | 15
Providing and fixing following type of surface rosette for sprinklers, of approved make. ( UL Listed and FM Approved)
Captive rosette
for 15 mm dia |  | 28
Providing and fixing 1.2 metre long braided stainless steel (grade AISI 304) flexible tubing suitable for fire sprinkler installation having 1" NPT mail thread inlet and 1/2" NPT female thread outlet. The unit shall be complete with bracket assembly for s | No | 16
Providing and fixing electric flow switch, capable of sensing a minimum of flow of one sprinkler, including making electrical cable termination.
For 80 mm dia sprinkler line | No | 1
Providing and fixing of nickel plated brass/ nonferrous alloy fully way ball valve ( minimum working pressure of 20 bar ) with operating handle of approved make. (Drain Valve)
25 mm dia. | No | 1
40 mm dia. | No
Providing and fixing Cast Iron butterfly valve as per IS: 13095 of Class PN 16, having epoxy coated disc, carbon steel shaft, EPDM rubber body liner and of approved make. including a set of MS flanges, required nos. of nut & bolts all complete.
100 mm dia with lever | No
80 mm dia with lever | No | 1
Dismentalling of following sizes existing sprinkler pipework including sprinkler heads as per site requirement including disconnecting, pluging,of pipes, upright/pendent sprinklers, fittings etc. (as per site Engineer). complete in all respect The mate
150 mm dia pipe | Rm
100 mm dia pipe | Rm
80 mm dia pipe | Rm
65 mm dia pipe | Rm
50 mm dia pipe | Rm
40 mm dia pipe | Rm
32 mm dia pipe | Rm
25 mm dia pipe | Rm
Providing & Tamper switch on main butter fly valve | Nos