## HVAC
WBS | Short Text | Description | UOM | Qty | Unit Price | Remarks
1.0 |  | EQUIPMENT
1 |  | AIR HANDLING UNITS (AHUs)
Ceiling Suspended type AHUs - With Non Thermal Break Profile
Supply, Installation, Testing and Commissioning of double skin air handling units (AHUs) each comprising of following as per the specifications :
a. |  | Casing of air handling units shall be in double skin construction. Inner skin shall be constructed out of 24 gauge plain GS sheet & outer skin in 24 gauge pre-plasticized GS sheet sandwiched between 25mm thick injected PU foam insulation of density not less than 40 Kg /CuM and complete with inspection doors including control wiring as required. AHUs shall have access for all parts.
b. |  | Fan section complete with forward curved DIDW type centrifugal fan/s, IE3, TEFC squirrel cage induction motor suitable to operate on 415+10%V, 50Hz, 3 phase AC power supply and belt drive package. Fan outlet velocity shall not be more than 1800 FPM (9.2MPS). Fan Motor shall be VFD compatible. Fan section should be completed with 25mm thick Armasound acoustic insulation. All fans should be AMCA certified.
c. |  | Coil section with multirows deep chilled water coil of copper tube & copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge stainless steel duly insulated. Face velocity across cooling coil shall not exceed 500FPM.
d. |  | Pre-Filter (EU-4) section complete with 50mm thick washable synthetic fiber filters. Velocity across the filters shall not exceed 500 FPM.
e. |  | AHUs shall be complete with suspension arrangement, it shall also include spring type vibration isolators and rubber grommets etc. to make the installation totally vibration free. AHUs shall have separate compartment for housing all valves.
f. |  | AHUs shall be provided with mixing chamber with S/A & F/A openings with dampers as per approved shop drawing.
g. |  | Multiblade box type zero leakage manually operated extruded aluminium volume control dampers shall be factory fitted at outlet of each AHU.
h. |  | In addition to the above, air handling units shall be provided with fire retardant flexible canvass connections made out of canvass sleeve. Sizes of air handling units shall not exceed as mentioned in the design drawings and air handling units shall conform to the design parameters mentioned in specifications.
The Air Handling Units (AHUs) shall be of following duty parameters :
AHU No Capacity S.P Motor Rows of Area to
(Cfm/TR) (mmWG) Rating coil be fed
(HP)
|  | CSAH-1 9/3600 35-36 Seating Area | Nos | 2
2 |  | VARIABLE FREQUENCY DRIVES
Supply, Installation, Testing and Commissioning of variable frequency drives for following Air Handling Units. Variable frequency drives shall be provided with necessary sensors and transmitters complete with control wiring in all respect as required and as per specifications. VFDs shall have built-in harmonic filters. The drives shall be suitable for the following motor rating. VFDs shall be housed in precoated, vandal proof enclosure with On/Off Push Buttons, Phase indication lights, A/M Switch and with adequate provisions for ventilation using a fan. The VFDs shall be able to receive the signals from multiple/combination of duct static pressure sensors/Temp. sensors and to ramp the speed of the motor.VFDs shall be suitable to take feed back and connectivity from all the DPS as mentioned below against each motor rating to facilitate averaging activity by VFD. Quoted price shall be inclusive of return air temperature sensor/Pressure Sensors and necessary electrical switches including change over switch & copper cabling for integration with the AHU panel. VFD panel shall be installed adjoining AHU panels for existing AHUs. Overall protection of VFDs with Panels shall be IP-54.
(i) Sensing Range : 10mm to 50 mm WG
(ii) Output Signal : 4 mA to 20 mA
OR
0 V to 10 V DC
|  | AHU - 3600 CFM | Nos | 2
|  | Exhust Unit - 8000 CFM | Nos | 1
|  | TFA Unit - 5000 CFM | Nos | 1
|  | Tube Axial Fan - 3000 CFM | Nos | 1
3 |  | EXHAUST UNIT WITH DRY SCRUBBER (For Kitchen Exhaust)
Providing & Fixing Cabinet type Exhust fan unit along with Electro static dry scrubber for kitchen exhuast to be fixed before exhust blower to eliminate the polluted air which comes out from kitchen.Cleair dry scrubber provide un equal performance in removing kitchen exhaust, smoke, oil, dust, particles and order. Techanical detaila as below: Casing of air handling units shall be in double skin construction. Inner skin shall be constructed out of 24 gauge plain GS sheet & outer skin in 24 gauge pre-plasticized GS sheet sandwiched between 25mm thick injected PU foam insulation of density not less than 40 Kg /CuM and complete with inspection doors including control wiring as required. AHUs shall have access for all parts. Fan section complete with forward curved DIDW type centrifugal fan/s, IE3, TEFC squirrel cage induction motor suitable to operate on 415+10%V, 50Hz, 3 phase AC power supply and belt drive package. Fan outlet velocity shall not be more than 1800 FPM (9.2MPS). Fan Motor shall be VFD compatible. Fan section should be completed with 25mm thick Armasound acoustic insulation. All fans should be AMCA certified. Cabinet - 1.2mm welded mild steel sheet Finish - Powder coated
|  | Air Flow - 8000 CFM ESP - 35MM Air Flow Type - Horizontal standard Installation type - Ceiling Suspended Construction to be closed from top and bottom with a basin for collection drain The pre-filter retains the large particles The particles in the airflow are charged P/N by the ionizing section Capacity Efficiency:-Up to 99% Prefilter:-Aluminum Mesh, Washable Electrical Rating:-Input Power:220~240W,, 50~60Hz. Make: Bry Air | Nos | 1
4 |  | Treated Fresh Air Unit ( TFA Unit) - CHW Type
Supply, Installation, Testing and Commissioning of double skin Treated Fresh Air units ceiling suspended type each comprising of following as per the specifications:
Casing of TFA units shall be in double skin construction with thermal break Aluminium profle section. Inner skin shall be constructed out of 24 gauge plain GS sheet & outer skin in 24 gauge pre-plasticized GS sheet sandwitched between 50mm thick injected PU foam insulation of density not less than 40 Kg /CuM and complete with inspection doors including control wiring as required. AHUs shall have access for all parts.
Fan section complete with forward curved DIDW type centrifugal fan/s, IE3, TEFC squirrel cage induction motor suitable to operate on 415+10%V, 50Hz, 3 phase AC power supply and belt drive package. Fan outlet velocity shall not be more than 1800 FPM (9.2MPS). Fan Motor shall be VFD compatible. Fan section should be completed with 25mm thick. Armasound acoustic insulation. All fans should be AMCA certified.
Coil section with multirows deep chilled water coil of copper tube & copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge stainless steel duly insulated. Face velocity across cooling coil shall not exceed 500FPM.
Pre-Filter section complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 450 FPM.
AHUs shall be complete with suspension arrangement, it shall also include spring type vibration isolators and rubber groomets etc. to make the installation totally vibration free. AHUs shall have separate compartment for housing of all valves or extended insulated auxiliary drain tray.
Multiblade box type zero leakage manually operated extruded aluminium volume control dampers shall be factory fitted at outlet of each AHU.
In addition to the above, air handling units shall be provided with fire retardant flexible canvass connections made out of canvass sleeve. Sizes of air handling units shall not exceed as mentioned in the design drawings and air handling units shall conform to the design parameters mentioned in specifications.
Suction side of the TFA unit should have flange for connecting duct from outside
The Air Handling Units (AHUs) shall be of following duty parameters :
AHU No Capacity S.P Motor Rows of Area to
(TR/Cfm) (mmWG) Rating coil be fed
(HP)
|  | CSAH-2 31/5000 35 BOH Area | Nos | 1
5 |  | TUBE AXIAL FAN
Supply,Installation,Testing and Commissioning of Tube Axial Fan of following as per the specifications:
Size: Upto dia 500mm CFM : 3000 CFM SP : 20mm Suitable for clean air normal ventilation and smokespill application Normal Ventilation: 100°C Motor: Totally enclosed Class 'F' or 'H', with a minimum IP55 protection are fitted as standard. Standard motor up to 2.2kW are supplied with DOL starting, motor 3.0kW and above are with star/delta starting Inlet and outlet duct connection flanges to connect circular duct to TDC flanges Vibration isolator mounts for floor or ceiling mounted installations A drain coupling to be attached to the bottom of housing Construction: Double flanged casing is produced in mild steel or galvanized steel. The impeller blades are of PPG, PAG, or Aluminium alloy Coatings: Zinc rich primer and polyester powder coating or galvanized finish for all mild steel parts.
M/c No Capacity S.P Motor Area to
(Cfm) (mmWG) Rating be fed
(HP)
|  | AS-1 3000 20 Kitchen FA | Nos | 1
1.5 |  | STARTER PANEL - SITC of starter panel DOL type. Panel must include the main MCB, phase indicating lamp, Over load relay & under over voltage relay, SPP, Tripping lamp etc. Panel should complete in all respect with MS fabrciated powder coated body. Wall mounted arrangement to be provided with hook. Earhting arrangement must be availalble. Cable entry should be available on top & bottom both side. starter panel should be complete with all installation & testing.NO/NC contact to be provided within the starter panel for tripping of AHU in case of fire. Intergration to be done with FAS panel
32 Amps ,TP MCB -- 1set
(0-500) V digital Voltmeter with built in Selectorswitch -- 1set
Digital Ammeter with built in selector switch- 1set
Current Transformers - 1set
LED type RYB phase indication lights- 1set
LED type ON & OFF indication lights -- 1set
3HP DOL starter with built-in single phasing
preventor & overload relay & adjustable timer -- 1 set
START-STOP Push Buttons -- 1 set
Auto-Manual type selector switch to facilitate auto start of AHUs -- 1set
|  | Contactors, Potential Free Contacts, Control wiring and safety circuit as required with start-stop push buttons stay put or lockable type -1set | Nos | 5
TOTAL ITEM NO. 1 (EQUIPMENT)
2.0 |  | PIPING AND VALVES
2.1 |  | CHILLED WATER PIPING
Supply , Installation, Testing and Commissioning of MS heavy class (Class "C') pipes cut to requird lengths and installed with all welded joints. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers, sockets etc., and hanging arrangement and floor supports as required, rigid PUF saddles, washers and check nuts etc in accordance with the approved shop drawings and specifications. All sleeves in Fire wall/slab shall be sealed using fireproof sealant.
For Pipe sizes of 80mm dia & above complete "C" channel support shall be provided. For floor supports, supports shall be complete with pipes of adequate size with base plate & vibration isolation pads and "C" channel. All pipe supports channels, fastner etc. to be selected as per support depth & loading as per structural consultant recommendations.
a |  | 80mm dia | RM | 80
b |  | 65mm dia | RM | 25
c |  | 50mm dia | RM
d |  | 40mm dia | RM | 20
e |  | 32mm dia | RM
2.2 |  | CONDENSATE DRAIN PIPING
CONDENSATE DRAIN PIPING -CPVC
Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc., and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form . Pipes shall be of following sizes :
a |  | 40mm dia | RM
b |  | 32mm dia | RM | 25
c |  | 25mm dia | RM | 20
2.3 |  | CHW Valve Assembly- Supplying , Installing , Testing and Commissioning of valve package included 5# Isolating Valve(Butterfly Valve), 1# Double Regulating Valve/Balancing valve, 1# Two way Motorized Modulating Valve, 1# Strainer, 2# Pressure Gauge, 2#Thermometer, 1#Drain valve, 2#Test Point Air vent as per drawing etc., complete as specified.
a |  | 80mm Dia | Nos
b |  | 65mm Dia | Nos | 1
c |  | 40mm Dia | Nos | 2
2.4 |  | FIRE STOPPING FIRE SEALING
|  | Sealing and fire stopping of vertical duct / pipe risers at each floor level with foam type Sealing System after installation of duct / pipe. Foam after solidifying shall have 2 hour fire rating. | SqM
2.5 |  | BMS INTERFACE
|  | Necessary sockets and nipples with shut off valves for mounting sensors/transmitters on pipe line to interface the BMS system. | Lot
TOTAL ITEM NO. 2 (PIPING & VALVES)
3.0 |  | DUCTWORK/AIR TERMINALS
3.1 |  | FACTORY FABRICATED / SITE FABRICATEDDUCTING
Supply, Installation and Testing of factory fabricated GSS (class VIII-120GSM Zinc Coaing) ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle/channel arrangement as required for ducts being installed outside or within building wherever required.
Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI "C" channels & Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct support to be provided with check nuts (lock nuts).
While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs.
Ducts shall be insulated Internally/externally as per approved shop drawing.
For Air-conditioning ducts
a. |  | 1mm to 750mm -- 24G GSS with TDC Joints | SqM | 55
b. |  | 750mm to 1200mm -- 22G GSS with TDC Joints | SqM | 15
c. |  | 1201mm to 1800mm - 20G GSS with TDC Joints | SqM
d. |  | 1801mm to 2100mm - 18G GSS with TDC Joints | SqM
e. |  | 2101mm to 2700mm - 16G GSS with TDC Joints | SqM
For Mechanical Ventilation ducts
a. |  | 1mm to 750mm -- 24G GSS with TDC Joints | SqM | 105
b. |  | 750mm to 1500mm -- 22G GSS with TDC Joints | SqM | 35
c. |  | 1501mm to 2100mm - 20G GSS with TDC Joints- For Scrubber Ducts | SqM
d. |  | 2101mm to 2700mm - 18G GSS with TDC Joints | SqM
Round Ducting
a. |  | 1mm to 750mm -- 24G GSS with TDC Joints | SqM | 35
b. |  | 750mm to 1200mm -- 22G GSS with TDC Joints | SqM
3.2 |  | FLEXIBLE CANVASS CONNECTIONS
|  | Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | SqM | 7
3.3 |  | Supply,Installation ,Testing and Balancing of double louvered supply air grilles as per approved shop drawings and specifications complete with key operated aluminium volume control dampers.
|  | a. Powder coated extruded aluminium grilles | SqM
3.4 |  | LINEAR GRILLES
Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade.
|  | Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces. | SqM
|  | 100 mm High grilles | Rmt
|  | 150 mm High grilles | Rmt | 20
|  | 200 mm High grilles | Rmt
3.5 |  | SUPPLY AIR DIFFUSERS (Square / Round)
a |  | Supply, Installation, Testing and Balancing of square supply air diffusers with removable key operated volume control dampers with opposed blades as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring type/flat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsum/grid ceiling. The diffusers shall be of regular type and with outer dimension of 450 x 450mm, 375mmx375mm & 300mmx300mm.
Powder coated extruded aluminium diffusers of approved colour & shade.
|  | Neck Size: 300x300 / Outder Size: 600x600 | Nos
|  | Neck Size: 375x375 / Outder Size: 600x600 | Nos
|  | Neck Size: 450x450 / Outder Size: 600x600 | Nos
|  | Neck Size: 600x600 / Outder Size: 600x600 | Nos
|  | 375 x 375 - FA Square Grill - Double Deflection Grill | Nos | 10
|  | 450 x 200 - FA Square Grill | Nos | 6
b |  | Supply, Installation, Testing and Balancing of Round supply air diffusers with 150mm high GSS plenum with spiggot to facilitate round flexible duct connections as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring type/flat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsum/grid ceiling. The diffusers shall be of regular type and with outer dimension of 600 x 600mm.
|  | Neck Dia : 300 & Outer Size: 375 | Nos
|  | Neck Dia : 375 & Outer Size: 425 | Nos | 5
|  | Neck Dia : 450 & Outer Size: 525 | Nos
C |  | RETURN AIR DIFFUSERS
Supply, Installation,Testing and Balancing of square return air diffusers same as supply air diffusers but without volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring type.
|  | Powder coated extruded aluminium diffusers of approved colour & shade. | Sq Mtr | 2
D |  | Supply, Installation,Testing and Balancing of square Fresh air double deflection grill with zero deg for spot cooling but with collar dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring /flat type.
|  | 375x375 Powder coated extruded aluminium diffusers of approved colour & shade suitable for fixing in grid ceiling. | No | 8
E |  | Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings.- For Rectangular Duct | SqM | 2
F |  | Supply, Installation and Testing of Aluminium multi blade type louver collar dampers as per the specifications and shop drawings of approved colour & shade. | SqM | 2
G |  | Supply, Installation,Testing and Commissioning of motorised fire dampers suitable for at least 90 minutes fire rating as per the specifications and approved shop drawings. Quoted price shall be inclusive of copper control wiring as required.
a. |  | Bare Fire Dampers | RO
b. |  | Spring return action type actuator complete with control panel and temperature sensor. Torque not less than 16NM | No
H |  | Supply, Installation and Testing of fresh air grilles of powder coated / anodised extruded aluminium with GI wire mesh, inlet louvers, Box type VCD & bird screen, as per the approved shop drawings and specifications.Double deflection fresh air grill with damper inside to adjust flow.
|  | 375x375 | Nos
I |  | Supply, Installation and Testing of Bird Screens with GI wire mesh to be installed at the suction of fresh air/discharge of Exhaust air as per the specifications and shop drawings. Sample of bird screen to be got approved from consultants and Clients prior to procurement. | SqM | 3
J |  | Supply, Installation and Testing of non return dampers. NRDs to be installed in the ducts as per the specifications and shop drawings.Sample of NRDs to be got approved from consultants and Clients prior to procurement. | SqM
K |  | Back Draft Damper - Supply, Installation and Testing of back draft damper on AHU mouth in GSS with periphery frame & blader. To be fixed in Nut & Bolt with flanges. | SqM
TOTAL ITEM NO.3 DUCTING AND TERMINALS
4.0 |  | INSULATION
4.1 |  | ACOUSTIC LINING OF DUCTS
Using Open Cell Nitrile Rubber
Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. Adhesive used shall be Low VOC type.
a. |  | 9mm thick lining | SqM
b |  | 13mm Thick | SqM
c |  | 25 mm thick | SqM | 45
4.2 |  | Using Fibre Glass
Supply and Application of internal acoustic lining of supply/ return air ducting using resin bonded fibre glass insulation of density not less than 32Kg/CuM as per the approved shop drawings and specifications. Quoted price shall be inclusive of GSS channel, metal screws, washers, fibre glass tissue, perforated aluminium sheet of 24G etc. as required for complete installation.
a. |  | 25mm thick lining | SqM
4.3 |  | THERMAL INSULATION OF DUCTS
Supply and Application of closed cell nitrile rubber thermal insulation for FA Duct/KEA Duct & Supply ducting (Inside the store) using aluminium foil faced closed cell elastomeric insulation with class 'O' fire retardant properties as per the specifications and drawings. Cladding shall provide protection from mechanical impact, ultra voilet radiations and Scratches etc. caldding shall not have any fibre erosion. Both insulation & cladding should have built in antimicrobial protection.
|  | 13mm Thick | SqM | 190
4.4 |  | CHW PIPE INSULATION
Using Closed Cell Elastomeric Insulation
Supply and Application of 25mm/32mm thick closed cell elastomeric insulation in tubing form /flat sections for chilled water piping as per the specifications. Quoted price shall be inclusive of adhesive as per specifications. Joints shall be sealed with adhesive forming proper bonding.Quoted price shall be inclusive of 24 G aluminium cladding for chilled water piping. (Adhesive - 1K PUR FR)
a. |  | 80mm dia (25mm thick) | RM | 80
b. |  | 65mm dia (25mm thick) | RM | 25
c. |  | 50mm dia (25mm thick) | RM
d. |  | 40mm dia (25mm thick) | RM | 20
e. |  | 32mm dia (25mm thick) | RM
TOTAL ITEM NO. 4 (INSULATION)
5.0 |  | ELECTRICAL WORKS
5..1 |  | CABLING
Supply, laying, affecting connections and Testing of the following sizes of 1.1 KV armored PVC insulated aluminium/ copper conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted price shall be inclusive of perforated duly painted 2mm thick MS trays to be installed inside and GI trays to be installed outside exposed and 8SWG copper earth wire for AHUs.All cables shall be FRLS type.
a |  | 3 C x 16 Sqmm cable (Copper) | RM
b |  | 3 C x 10 Sqmm cable (Copper) | RM
c |  | 4 C x 6 Sqmm Ar. Cable (Copper) | RM | 30
d |  | 4 C x 4 Sqmm Ar. Cable (Copper) | RM | 90
e |  | 3 C x 2.5 Sqmm cable (Copper) | RM
f |  | 3 C x 2.5 Sqmm cable( Copper Control cabling) | RM
g |  | 3 C x 1.5 Sqmm cable(Copper Control cabling) | RM
h |  | 4 C x 1.5 Sqmm cable( Copper Control cabling) | RM
5.2 |  | Supply of Installation of Following Cable Terminations including Single/Double compression type chrome plated brass glands and lugs(crimping type), PVC taping as required and all accessories complete.
a |  | 3 C x 16 Sqmm cable (Copper) | Nos
b |  | 3 C x 10 Sqmm cable (Copper) | Nos
c |  | 4 C x 6 Sqmm Ar. Cable (Copper) | Nos | 4
d |  | 4 C x 4 Sqmm Ar. Cable (Copper) | Nos | 6
e |  | 3 C x 2.5 Sqmm cable (Copper) | Nos
f |  | 3 C x 2.5 Sqmm cable( Copper Control cabling) | Nos
g |  | 3 C x 1.5 Sqmm cable(Copper Control cabling) | Nos
h |  | 4 C x 1.5 Sqmm cable( Copper Control cabling) | Nos
TOTAL ITEM NO. 5 (ELECTRICAL WORKS)
6 |  | MISC ITEMS
6.1 |  | DRAIN PUMP
|  | Providing & fixing Drain Pump in heavy efficiency for 5700 CFM AHU unit including with fitting Etc. | Nos.
6.2 |  | Lifting equipment by Staircase
|  | Making suitable arrangement for lifting & placing of Scrubber, Air washer units from ground Floor to the mall 7th floor terrace area..Unit to be brought in dismantle condition. Assemnly to be done on site | L/S
TOTAL ITEM NO. 6 (MISC ITEM)
TOTAL
ADD GST18%
GRAND TOTAL