## HVAC UNPRICED BOQ
AJ KITCHEN- 1881CAFE
SUBJECT : HVAC WORKS UNPRICED BOQ
REVISION -R0
SL. NO. | ITEM DETAILS | UNIT | QTY | SUPPLY RATE | INSTALLATION RATE | TOTAL AMOUNT
|  |  |  | INR | INR | INR
MECHANICAL SYSTEM
AIR CONDITIONING WORKS
Supply, Installation, Testing & Commissioning & Handing over of the following:
PREAMBLE TO BOQ:
Tendered Rates all Inclusive:
Unless otherwise provided in the Bill of Quantities, the rates tendered by the Contractor for all items of the work shall be all inclusive and shall apply to all heights, lifts, leads and depths, in all positions of the building.
1 | CHILLED WATER TYPE DOUBLE SKIN AIR HANDLING UNITS - CEILING SUSPENDED TYPE
Supply,Installation, Testing & Commissioning of Double skin type Ceiling suspended units complete with double skin (43±3 mm) insulated with CFC free polyurethane foam (PUF) panels of 40 +/- 2 Kg/cum density. The outer and inner panel thickness shall be 0.8 mm and 0.63 mm GI respectively. Outer skin shall be precoated/Powder Coated G.I. sheet and internal skin shall be Plain G.I. sheet suitable for chilled water application. The unit shall be provided with DIDW Fan, Motor, minimum 4 row cooling coil and drain pan with 15mm thick nitrile rubber insulation, inlet filter section with with 50mm thick panel type pre-filter of MERV-8 as part of CSU, drive set & guard, spring isolator to avoid transmission of vibration,etc. The noise of the unit shall not exceed more than 55-60 dBA at 1m distance from the unit and at maximum operating speed.The height of the unit shall not exceed 650mm. Additional FRP drain tray shall be considered for this units. Cooling Coil should be certified by AHRI 410
The unit shall be provided with belt driven backward curved Multi fans for achive the unit hight as not Exceed 650mm, IE3 Motor, drive package, vibration isolating rubber bush to fans and motor to avoid transmission of vibration. All CSU motor pulleys shall be of adjustable type only. Cost shall be inclusive of non-cloth type canvas connection made of self extinguishing, moisture resistant flexible fabric to be provided between CSU outlet flange and the supply duct / plenum.Spring isolators shall be used in the installation of the Ceiling suspended Units to ensure there is no transmission of vibration from the equipment to the building structure.
a | Supply. Installation,Testing & Commissioning of Double Skin CSU- Capacity-5 TR capacity, 1750 Dcfm with 0.325 sqm cooling cooling coil face area, 30 mmwg fan external static, 4/6 row cooling coil, 0.75/1.1 Kw fan motor, filter section with Pre Filter (EU-3)-MERV-8 supplied by the builder -Serving area: AJ Kitchen - Fine Dine | Set | 1 | 60000 | 5000 | 65000
b | Supply, Installation, Testing & commissioning of Limit switch wiring ,lighting & motor interlock to be provided with 3 core 2.5sqmm cable in 19mm dia GI conduit | Rmt | 20 | 1700 | 500 | 44000
2 | CHILLED WATER PIPING WITH INSULATION |  |  |  |  | 0
Supply, Installation, Testing & commissioning of MS 'C' Class pipes insulated with Closed cell elastomeric insulation of specified thickness & Insulation to be covered with Aluminium cladding 26G , 0.5mm thick as per technical specification. All Bolts / Nuts used in the chilled water piping should be of GI & not MS. The cost shall be inclusive of pipe suppoorts with MS Channels. The piping flange connection bolts, washers and nuts should be hot dipped galvanised.The pipes should be supported with MS Channels, angle frame with neoprene rubber / PUF saddles. Fitting accessories for installation of pressure gauges, thermometers, BMS sensors, drain ports to be provided by the HVAC lowside contractor. Flourscent Plastic Sticker/ paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. "Table E" of BS code for flange thickness to be adhered. The Piping material & network should be selected to operate at PN 16 Rating
Pipe dia below 150 mm shall be C Class confirming to IS:1239 (part 1) 2004,Pipe size between 200 mm to 350 mm dia shall be 6.35 mm & pipe dia above 350 mm shall be 8.0 mm confirming to IS:3589 Gr330
Opening and closing for all the chilled pipe entries in civil / gypsum / any type of partition shall be under scope of HVAC vendor and inclusive of cost. Routing diagram can be checked in drawing prior for quoting.
b | 32 mm dia | Rmt | 20 | 2200 | 500 | 54000
3 | BUTTERFLY VALVE WITH INSULATION
Supply, Installation, Testing & commissioning of Wafer type Butterfly valve which shall be of Slim seal wafer type with long stem of PN 16 rating, companion flanges shall also be of PN20 rating. Butterfly valves installed for the chilled water pipelines shall be insulated with nitrile rubber insulation and the insulation thickness shall be similar to that of the pipe dimensions. (valve sizes above 200mm shall be wheel operated type instead of handles). All bolts, washers and nuts shall be hot dipped galvanized only.The MOC of body shall be cast iron & disk shall be epoxy coated ductile iron.
b | 32 mm dia | Nos | 5 | 8000 | 2000 | 50000
4 | PRESSURE INDEPENDENT TYPE DYNAMIC BALANCING CUM FLOW CONTROL VALVE.
Valve selection to be submitted in the technical submittal for approval before procurement.
Supply, Installation, Testing & commissioning of Pressure Independent dynamic balancing cum equal percentage type modulating flow control valve - PN16 rating fitted with high torque actuator with Non spring return type to ensure the valve closes automatically in the event of power disconnect to actuator. Actuator enclosure shall be rated for IP 54 protection. Step down transformer if required shall be part of valve supply, matching flanges, hot dipped galvanized bolts and nuts. Valve body to be insulated with closed cell elastomeric insulation. Supply , Installtion, testing & commissioning of thermostat along with control/ power cabling to be part of scope.The MOC of body shall be cast iron & membrane shall be EPDM, SS spring.
Actuator should be provided with position feed back switch and also actuator should have BMS interfacing card and shall be suitable for accepting signals from temperature sensors supplied by BMS vendor. Actuator should also have facility to set the required flow rate as per site requirements through dip switch adjustments. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with +/- 5% flow accuracy. THe scope shall include the cost supply of thermostat/ return air temperature and required control cabling
Valve shall have necessary measuring ports, drain port, flanges etc., The balancing to be done through microprocessor based hand held terminal / POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
b | 32 mm dia | Nos | 1 | 11500 | 2000 | 13500
6 | TEMPERATURE SENSORS
| Supply, Installation, Testing & commissioning of Duct type/ space type temperature sensor for measuring the Return air temperature at the Chilled water type CSU Units (Range 45-150 deg. F).A Temperature sensor shall be provided in the return air path of CSU to control the 2 way modulating valve. The scope shall include the cost of Control Cabling with conduit between temperature sensor and actuator of 2 Way modulating flow control valve | Nos | 1 | 4000 | 500 | 4500
7 | Y'-STRAINER WITH INSULATION
Supply, Installation, Testing & commissioning of Y-strainer -PN 16 rating body construction shall be with Mild steel and strainer shall be of SS screen with permanent magnet and drain port. The MOC of body shall be cast iron & SS-304 filter with 3 mm perforation with flanged connection, gaskets, permanent magnet. Note, the insulation quantity will be measured in running meters and the valve in numbers.
b | 32 mm dia | Nos | 1 | 4000 | 500 | 4500
9 | TEMPERATURE GUAGES
a | Supply, Installation, Testing & commissioning of Thermometer which shall be of Dial type (100mm) Range 0⁰ to 50⁰C, with stainless steel body - IP 55 protection, with necessary theromowells. | Nos | 2 | 5500 | 1000 | 13000
10 | PRESSURE GAUGE (GLYCERINE FILLED)
a | Supply, Installation, Testing & commissioning of Pressure Gauge which shall be of Bourdon tube Dial type (100mm) Range 0 to 10 kg/cm², with stainless steel body - IP55 protection with necessary pipe fitting and needle valve etc., | Nos | 2 | 7200 | 1000 | 16400
11 | INSULATED RIGID PVC PIPING FOR CONDENSATE DRAIN
Supply, Installation, Testing and Commissioning of Rigid PVC piping with pressure rating of 6 Kg /CM2 duly insulated with 9 mm thick factory laminated aluminium foil faced closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties in tubing form & all fittings, elbows, tees reducers, supports and clamps up to 50 mm dia. including drilling, wall chipping etc. and conceal the wall opening. Pipes shall be of following sizes :
a | 65mm. Dia. | Rmt | 30 | 500 | 100 | 18000
b | 50mm. Dia. | Rmt | 15 | 400 | 100 | 7500
c | 40mm. Dia. | Rmt | 20 | 300 | 100 | 8000
13 | DRAIN VALVES
Supply, Installation, Testing & commissioning of Ball/Drain valves with handles and extended stem , threaded joints shall be of PN16 class and insulated with nitrile rubber.The MOC of body shall be forged brass, SS ball, SS 410 stem. The end connections shall be threaded.
a | 25 mm dia | Nos | 2 | 1700 | 500 | 4400
14 | GSS DUCT WORKS
FACTORY FABRICATED DUCTING - TDF /TDC FLANGES - RECTANGULAR DUCTWORKS
Supply, Installation, Testing & Commissioning of factory fabricated GSS Ducting with TDF /TDC flange with GI bolt & nuts (the cleat into the flange Used for C and G together with Bolt) and necessary supporting arrangement using GI full threaded rods and slotted rail- Unistrut channel supports of size 41mm x 41mm for rectangular ducts to be used
Ducting shall include guide vanes etc., Ducting shall be designed for 500pa ESP as per the specifications, GSS Ducting:- Galvanized steel sheet shall be of Class VIII – light coating of zinc, nominal 120 gm /sqm as per IS-277.All ducts 900 mm to 1100mm shall have Stiffener bracket made of GI 1.25mm thick sheet and 1101mm above shall have Stiffener bracket made of GI 1.6mm thick sheet with special profile for strength and rigidity fixed throughout the duct perimeter Intermediate between flanges with Fastener screws 2 nos for every interval of 150mm.
Spacing between duct supports should not exceed 2m i.e GI rods with GI "C" channels. In case of duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct support to be provided with check nuts (lock nuts).
While selecting the duct supports vendor shall ensure vibration free installation. Quoted price shall be inclusive of light testing with complete arragement & accessories for leakages. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supports including MS angle/channel arrangement as required for ducts being installed outside or within building wherever required.
All duct construction and installation shall be in accordance with SMACNA standards. In addition ducts shall be factory fabricated utilizing the following machines to provide the requisite quality of ducts.
b | 24 G-GSS-0.63MM ( 251MM TO 1000MM) - TDF Flanges | Sqm | 105 | 1300 | 500 | 189000
c | 22 G-GSS-0.80MM ( 1001MM TO 1200MM) - TDF Flanges, Guide Vanes & Stiffeners Rods | Sqm | 2 | 1500 | 500 | 4000
15 | DUCT INSULATION MATERIALS
15.1 | THERMAL INSULATION FOR DUCTWORKS
Supply, Installation, Testing & Commissioning of Thermal insulation closed cell elastromeric nitrile rubber insulation manafactured as per ASTM E 84 test with density between 40-60 kg / m³(External and internal) for spiral duct, Material shall be FM GLOBAL approved, food grade material with antimicrobial properties, Class 'O'. Insulation material should meet NFPA 90A supplementary materials for air distribution system which should not absorbs less 0.2% water by volume (ASTM c 209), should not support microbial growth (ASTM C1071, G21, G22) and should emit objectionable odors (ASTM C 665) and should have thermal conductivity of 0.27 ( R - 2.78 in 3.4" thickness) and water vapor permeance of 0.10. Scope shall include the cost for aluminium foil which to be laid over the thermal insulation. Aluminium foil shall provide protection against scratches.
Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet.Insulation materials brought on site should be installed following the manufacturer recommended methodology and using the appropriately suitable manufacturer recommended cutting, measuring, pasting tools & tackles. It is advised to use the manufacturer’s tool box for installation of insulation materials on site.
b | 13mm thick | Sqm | 65 | 80 | 25 | 6825
15.2 | ACOUSTIC INSULATION FOR DUCTWORKS
SITC of internal acoustic lining within air ducts plenum with open cell 10mm thick Elastromeric nitrile rubber insulation manafactured as per ASTM E 84 test with density140- 180 kg / m³, Material shall be FM rated as per the approved shop drawings / specifications. Insulation material should meet NFPA 90A supplementary materials for air distribution system which should not absorbs less 0.2% water by volume (ASTM c 209), should not support microbial growth (ASTM C1071, G21, G22) and should emit objectionable odors (ASTM C 665) and should have thermal conductivity of 0.27 ( R - 2.78 in 3.4" thickness) and water vapor permeance of 0.10. - Class "1" Material.
Insulation sheets should have self-adhesive backing for faster installation and better quality. The adhesive used in self-adhesive backing should be Fire Retardant, LEED compliant and zero VOC.
Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet.Insulation materials brought on site should be installed following the manufacturer recommended methodology and using the appropriately suitable manufacturer recommended cutting, measuring, pasting tools & tackles. It is advised to use the manufacturer’s tool box for installation of insulation materials on site.
a | 10mm thick-acoustic insulation for main duct outlets as per HVAC drawings | Sqm | 7 | 3200 | 250 | 24150
0
16 | AIR DISTRIBUTION DEVICES
16.1 | MANUAL TYPE VOLUME CONTROL DAMPERS
a | Supply, Installation, Testing & Commissioning of Volume Control Dampers made out of 100 x 40 x 1.55 mm thick galavanised steel frame and blades of 1.55 mm galavanised sheet steel. | Sqm | 0.7 | 4000 | 500 | 3150
16.2 | ALLUMINIUM COLLAR DAMPERS
a | Supply, Installation, Testing & Commissioning of Collar Dampers or neck damper of opposed blade type made out of Aluminium alloy extrusion with anodised matt black finish (AL.blade thickness 1.0mm, Border thickness-1.3 MM). Qty is for Supply air grilles | Sqm | 1.7 | 4000 | 500 | 7650
16.3 | CONTINUOUS LINEAR GRILLE
Supply, Installation , Testing & Commissioning of Extruded Al. powder coated continuous, discrete grilles for supply & return air distribution of 100 to 600 mm wide with 0 / 15 / 30 / 45 deg (AL.frame thickness 1.2MM, Louver thickness-3 MM). Deflection as specified In the approved shop drawings. Grilles complete with integral flanges on both sides & ends as required complete with corner pieces.( colour for the grill to be conifremed by Arch/ PMC team before placing the order)
a | 150mm wide | Nos | 21 | 900 | 200 | 23100
16.4 | POWDER COATED ALUMINIUM GRILLES- FOR EXHAUST AIR & FRESH AIR APPLICATION
Supply, Installation , Testing & Commissioning of Extruded Al. powder coated grilles for exhuast air & Fresh air application with 0 degree deflection. AL.frame thickness 1.2MM, Louver thickness-1MM/ 3 MM ( colour for the grill to be conifimed by Arch/ PMC team before placing the order). The sizes of the grilles shall be as mentioned below
a | 600mm x 600mm | Nos | 3 | 2400 | 500 | 8700
b | 200mm x 200 mm | Nos | 2 | 2000 | 500 | 5000
16.5 | 4 WAY SUPPLY AIR DIFFUSERS- SQUARE TYPE
Supply, Installation , Testing & Commissioning of Powder coated, extruded aluminium, removable center core type, supply air diffusers with Collar Dampers or neck damper of the following neck sizes.
(All are of 595 x 595 MM Outer to Outer Size)
b | 300 x 300 MM (Neck Size) | Nos | 1 | 1500 | 500 | 2000
17 | ELECTROSTATIC DRY SCRUBBER FOR KITCHEN EXHAUST OF 3600 CFM.
Supply, installation, testing & Commissioning of Electro- Static DRY scrubber for the above exhaust rating of 3600 CFM. The vendor shall include the Pressure drop to be 20mm Wg, works with necessary valve arrangement. The scope of supply should include complete system for Electrostatic Dry scrubber operation. It shall also include the carbon filters for residual carbon content removal.The Electrostatic Air Cleaners shall be supplied as a one-piece factory joined assembly of individual section(s) selected to treat oil mist, smoke, fume, grease & dust/ powder problems.
Housing shall be constructed with minimum 1.6mm thick steel sheet with reinforced structure & powder coated to protect against rust and corrosion. It shall have a hinged door for cell access, located one side of the unit. The door shall be gasketed to prevent air leakage. There shall be a safety interlock switch to cut off primary supply when the access door is opened.The external finish shall be a durable industrial grade semi-gloss epoxy-polyester coating suitable for outdoor installations.
Ionizing-Collecting cell(s) shall be of one-piece construction 13.38” (340mm) deep in direction of airflow. The dimension of the collection cell shall be 18.89” (480mm) H x 19.76” (502mm)W Max. All support framing, end plates and ionizer ground electrodes shall be 0.080 inch (2mm) thick aluminum. Both repelling and collector plates shall be 0.032 inch (0.8mm) thick aluminum alloy material rigidly retained in place with tubular spacers and tie rods. Each plate shall be corrugated, perpendicular to airflow direction. Spacing between plates shall be no less than 0.318 inch (8mm). Each cell shall weigh at least 17 kg with at least 8 stainless steel spiked blade ionizers. Tungsten wire ionizers will not be accepted
Ionizing spiked blade shall be made of Stainless steel 304 material, rigidly supported both vertically and laterally. Spiked ionizer to ground electrode spacing shall be 1.0" (25mm). High voltage support insulators shall be of Teflon material for dielectric strength.
Equipment should be selected on the basis of required Air handling capacity so as to achieve 90-95% particulate matter removal efficiency according to DOP Test or EN779 European standard (Equivalent to ASHRAE 52.1). Vendor should submit the Test report from the Lab having Test facility according to ASHRAE 52.2 or EN779. In the absence of Test report Vendor should demonstrate the efficiency claim at their manufacturing facility at their expenses.
Power supplies shall be 100% solid state, operate on 230 VAC, 50 Hz, 1 Phase input and provide a dual high voltage output of 12-13 KVDC for the ionizer and 6.0-6.5 KVDC for the collector in normal operation conditions. Current output at the high tension shall be 12mA. A maximum power output for the solid state power supply shall be 120 watts to maintain the specified collection efficiency. Integrally mounted Electrical interlocks shall be provided to prevent access to the high voltage components without first interrupting the primary input power. The power supply shall operate over a temperature range of -32 degrees F to 140 degrees F, be overloaded self-protecting and accommodate an LED lights indicating the performance status of the ionizing/collecting cell. High voltage output components in the power supply shall be sealed with epoxy for moisture resistance.
The power pack shall incorporate a short circuit arc protection with automatic power restoration system to prevent overload.
There shall be 2 LED lights (Green & Red) installed on the access door of the unit to indicate the status of the air cleaning system
BMS (Building Management System) interface: The power supply (pack) shall have a 2 wire dry contacts (NO/NC) for remote link to Building Management System. This is for performance indication of the air cleaning system
| Supply , Installation , Testing & Commissioning of Electro-static Dry Scrubber unit complete with all sections as listed above & detailed in tender drawings | Nos | 1 | 70000 | 5000 | 75000
| TOTAL |  |  |  |  | 651375
| GST -18% |  |  |  |  | 117247.5
| GRAND TOTAL ( INCLUDING GST) |  |  |  |  | 768622.5
EXCLUSIONS
1 | TAXES SHALL BE EXTRA AS APPLICABLE
2 | ANY CIVIL WORKS LIKE WALL OPENINGS , WALL CLOSURE & PLASTERING WORKS RELATED TO HVAC ARE BEEN EXCLUDED FROM HVAC SCOPE OF WORKS.
3 | ALL ELECTRICAL WORKS( OTHER THAN INCLUDED IN HVAC BOQ) INCLUDING PANELS, CABLING, FEEDERS, CABLETRAYS ETC ARE BEEN EXCLUDED FROM HVAC SCOPE OF WORKS.

## EXCLUSIONS (hidden)
Architectural Exclusions:
1. Interior Finishes and Ceiling Finishes are not included other than BOH, Staircases and Services room. Since those areas are part of Interior Consultant
2. All Hotel Suite room finishes are not included since it is part of Interior Consultant
3. Only BOH area, Staircases, Service room and External doors & joinery are included. All other interior doors & joineries are by Interior Consultant
4. Sliding and folding partitions at Convention halls and Banquet halls not included since it is part of Interior Consultant
5. All Internal Furniture and Fit-out is not included since it is part of Interior Consultant
6. Kitchen, Laundry, House Keeping Equipment is not included since it is part of Kitchen and BOH Consultant
7. All Internal signage’s and graphics is not included since it is part of Interior scope
8. Decorative hanging ceiling such as Fabric hanging, Timber beam, Mesh weave, Interior curtains is not included since it is part of Interior scope.