## Fire and Life Saftey
Project Name : AJ Kitchen_Mumbai | [7 empty] | Date : 11.04.2024
Fire Alarm, Extinguisher Fire Signage,Fire Sprinkler and PA System | [7 empty] | Rev No : R0
Sl No | ITEM DESCRIPTION | UNIT | QTY | Rate |  | Amount |  | Remarks
|  |  | Total | Supply | Installation | Supply | Installation
1 | FIRE Alarm System Works
1.2 | Supply installation testing and commissioning of addressable type smoke detectors with LED indication lamp, MS Back box, detector base braket, along with complete fixing accessories.(Below false ceiling) | Nos | 4 | 2300 | 1500 | 9200 | 6000
1.2a | Supply installation testing and commissioning of addressable type Multi Sensor Heat detectors with LED indication lamp, MS Back box, detector base braket, along with complete fixing accessories. | Nos | 3 | 2000 | 1000 | 6000 | 3000
1.4 | Supply installation testing and commissioning of addressable Hooter cum STROBE along with its control modules complete with all fixing materials. | Nos | 1 | 3000 | 1500 | 3000 | 1500
1.5 | Supply and installation of analogue addressable type Manual call points with Glass and hammer and monitor module with complete fixing accessories also with self illuminated signage. | Nos | 1 | 2600 | 1500 | 2600 | 1500
1.7 | Supply and installation of Monitor Module with complete fixing accessories | Nos | 1 | 4500 | 1500 | 4500 | 1500
1.8 | Supply and installation of Control Relay Module with complete fixing accessories | Nos | 1 | 3800 | 1000 | 3800 | 1000
1.9 | Supply and laying of PVC insulated,2C x 1.5sq.mm shielded armored FRLS copper cable (RED COLUR) including cable glands and all fixing accessories where ever required complete with end terminations at both sides. The colour of the cable shall be RED only.( Shall be on actuals ). | Rmtrs | 50 | 60 | 10 | 3000 | 500
1.10 | Supply, installation, testing and commissioning of Addressable fire alarm Panel which consists of display board which will have 160 Character Display with Touch key pad, Mother board which will have ARM CORTEX M3 32 Bit Processor, Inbuilt RS-485 Networking Circuit for peer to peer networking, Inbuilt USB 2.0 Port for upload and download the Configuration tools, Two inbuilt programmable inputs, Two inbuilt NAC's, and Three Programmable Relays, and 4 Loop Card circuits. power Supply, Installation and Commissioning Board which will have SMPS fully protected board, which its operates on 120 to 220V AC ± 10% with 50/60 Hz, battery backup 24V DC with built-in charger. the panel have IP-50 rating Optional: for BMS integration thru MODBUS converter, Graphical Software, Software for TCP/IP Module, provision for GSM based Auto dialler, provision for printer thru compatible module, fire alarm panel with battery backup for 6 hours operation, with battery charger, alarm bell, test buttons etc.
a | 2 loop panel | Nos | 1 | 42500 | 5000 | 42500 | 5000
1.11 | SITC of Hand held Fire Extinguisher - ABC Powder - 6 Kg with floor mount accessories | Nos | 2 | 6000 | 1000 | 12000 | 2000
1.12 | SITC of Hand held Fire Extinguisher - CO2 - 4.5 Kg with floor mount accessories | Nos | 2 | 11000 | 1000 | 22000 | 2000
1.14 | Supply installation testing and commissioning of Fire Exit - LED Battery Backup (180Min) | Nos | 3 | 2500 | 500 | 7500 | 1500
2 | PA System Works
2.2 | Supply and installation testing and commissioning of 6 Watt Recesse Mounted Ceiling speakers along with all fixing accessories . | Nos | 4 | 5400 | 1000 | 21600 | 4000
2.3 | Supply and laying of shielded twin twisted pair 1.0 sqmm cable in existing conduit ( Shall be on actuals ). | Rmtrs | 50 | 80 | 10 | 4000 | 500
2.4 | Supply and fixing of 20mm dia heavy guage GI conduit concealed in wall/ above false ceiling for taking copper wires including all accessories such as Conduit junction boxes, bends etc as required ( Shall be on actuals ). | Rmtrs | 40 | 160 | 50 | 6400 | 2000
2.6 | Mixer Amplfier -120W with Pre recorded Message ,Music Ssytem etc complete in a PA rack (The rate to include the Cost of rack and other required acessories ) | Nos | 1 | 70000 | 5000 | 70000 | 5000
| Total Amount |  |  |  |  | 218100 | 37000 | 255100
TAX
GRAND TOTAL - SUPPLY + INSTALLATION +TAXES