## Fire and Life Saftey
Project Name : AJ Kitchen_Mumbai | [7 empty] | Date : 11.04.2024
Fire Alarm, Extinguisher Fire Signage,Fire Sprinkler and PA System | [7 empty] | Rev No : R0
Sl No | ITEM DESCRIPTION | UNIT | QTY | Rate |  | Amount |  | Remarks
|  |  | Total | Supply | Installation | Supply | Installation
3 | Fire Sprinkler System:
3.1 | Supply, installation, testing and commissioning of G.I Heavy grade piping as per IS: 1239/3589 GI Forged Threaded GI forged socket welded & 65mm and above Seamless schedule 40) with necessary fittings such as tees, elbows,union,flanges, bends, rubber gaskets, reducers, GI nut bolt, washer etc. The pipes being suspended from ceilings by using support with clamps, hangers using anchor fastners upto 65 mm & above 80 mm pipe should be support with galvanized channel supports complete Rate quoted shall include painting with one coat of zinc cromet primer & 2 coats of synthetic enamel PO red paint and for painting of pipe & brackets and clamps as per IS-5 for above ground piping as per the NBC / IS standards and local fire service department requirement complete including supply and installation of G.I. Rods, clamps and , fasteners etc. All supports shall be hot dip galvanized in the range of DFT of micron 80 to 90 micron with 7 tank process, hot dip galvanizing shall be confirming to IS:2629/2633/4759/6745. Anchor fastners to be used of chemical type only where pipe supports to be taken from brick/block work.
g | 32mm nominal dia | Rmtrs | 3 | 450 | 150 | 1350 | 450
h | 25mm nominal dia | Rmtrs | 30 | 350 | 150 | 10500 | 4500
3.2 | Supplying, installing, testing and commissioning conventional Standard Response Sprinkler quartzoid bulb type with 15mm screwed end connection of 68 deg. C. temperature rating, K-Factor =5.6 GPM/psi½ (80.6 LPM/bar½) and orifice shall not be less than 6mm. Sprinklers shall be UL Listed / BIS approved with Chrome finished.
b | Concealed Sprinkler | Nos | 16 | 2000 | 1000 | 32000 | 16000
3.3 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be 16 bar pressure rating and 1500 mm long, 25 mm dia with union / reducer collar, clamps etc. as required. | Nos | 16 | 1300 | 500 | 20800 | 8000
3.4 | Supply & fixing of approved type rosette plates (Recessed type, in two piece) for Sprinklers below false ceiling area. | Nos | 16 | 70 | 20 | 1120 | 320
| Total Amount |  |  |  |  | 65770 | 29270 | 95040
TAX
GRAND TOTAL - SUPPLY + INSTALLATION +TAXES